## Summary Table
Turn off all excluding C & D grades
Row Labels | Count of CONDITION RANK | Average of Estimated Remaining Useful Design Life (YEARS) | Sum of Year 1 - 2018/19 | Sum of Year 2 - 2019/20 | Sum of Year 3 - 2020/21 | Sum of Year 4 - 2021/22 | Sum of Year 5 - 2022/23 | Sum of Total | Row Labels | Average of Likelihood Score (1-4) | Average of Consequence Score (1-5)
Protection Systems | [8 empty] | Ceiling Finishes
Fire Alarm Installations (inc, call points, sounders and detection) | [8 empty] | Mineral fibre suspended ceiling tiles 600 x 600
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Fire Alarm Installations (inc, call points, sounders and detection) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Protection Systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Mineral fibre suspended ceiling tiles 600 x 600 Total | 2.6571 | 2
Ceiling Finishes | [8 empty] | Suspended Ceiling Tile - Metal
Mineral fibre suspended ceiling tiles 600 x 600 | [8 empty] | MODERATE | 3 | 2
B | 43 | 9.7674 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 35 | 2.6286 | 0 | 19956.3759 | 15934.8186 | 0 | 0 | 35891.1945 | Suspended Ceiling Tile - Metal Total | 2.5 | 2
A | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Mineral fibre suspended ceiling tiles 600 x 1200
Mineral fibre suspended ceiling tiles 600 x 600 Total | 83 | 7.494 | 0 | 19956.3759 | 15934.8186 | 0 | 0 | 35891.1945 | MODERATE | 3 | 2
Suspended Ceiling Tile - Metal | [8 empty] | Mineral fibre suspended ceiling tiles 600 x 1200 Total | 3 | 2
B | 10 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | Bulkhead (tiles)
C | 2 | 2.5 | 0 | 134 | 670 | 0 | 0 | 804 | MODERATE | 3 | 2
A | 3 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | Bulkhead (tiles) Total | 3 | 2
Suspended Ceiling Tile - Metal Total | 15 | 13.4667 | 0 | 134 | 670 | 0 | 0 | 804 | Ceiling Finishes Total | 2.6829 | 2
Exposed underside of stair | [8 empty] | Comfort Cooling
B | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Computer room air conditioning
Exposed underside of stair Total | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Exposed Concrete | [8 empty] | Computer room air conditioning Total | 2 | 2
A | 8 | 57.5 | 0 | 0 | 0 | 0 | 0 | 0 | Comfort Cooling Total | 2 | 2
Exposed Concrete Total | 8 | 57.5 | 0 | 0 | 0 | 0 | 0 | 0 | Cubicles
Mineral fibre suspended ceiling tiles 600 x 1200 | [8 empty] | High Pressure Laminated Chipboard
B | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
C | 3 | 2 | 0 | 5811.72 | 0 | 0 | 0 | 5811.72 | LOW | 2 | 2
Mineral fibre suspended ceiling tiles 600 x 1200 Total | 10 | 7.6 | 0 | 5811.72 | 0 | 0 | 0 | 5811.72 | High Pressure Laminated Chipboard Total | 2.75 | 2
Metal suspended ceiling tiles 600x1200 | [8 empty] | Cubicles Total | 2.75 | 2
B | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | Decorations
Metal suspended ceiling tiles 600x1200 Total | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to walls
Plasterboard & Skim finish | [8 empty] | MODERATE | 3 | 2
B | 16 | 14.625 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Plasterboard & Skim finish Total | 16 | 14.625 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to walls Total | 2.6111 | 2
Exposed Soffit | [8 empty] | Emulsion paint finish to Ceiling
B | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
A | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to Ceiling Total | 3 | 2
Exposed Soffit Total | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | Decoration of timber surfaces
Timber boarding | [8 empty] | LOW | 2 | 2
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Decoration of timber surfaces Total | 2 | 2
Timber boarding Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery decorations (architraves, skirting)
MDF Boards | [8 empty] | MODERATE | 3 | 2
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
MDF Boards Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery decorations (architraves, skirting) Total | 2.5 | 2
Bulkhead (tiles) | [8 empty] | Timber surround to rooflight
C | 1 | 2 | 0 | 458.82 | 0 | 0 | 0 | 458.82 | LOW | 2 | 2
Bulkhead (tiles) Total | 1 | 2 | 0 | 458.82 | 0 | 0 | 0 | 458.82 | Timber surround to rooflight Total | 2 | 2
Ceiling Finishes Total | 142 | 12.4789 | 0 | 26360.9159 | 16604.8186 | 0 | 0 | 42965.7345 | Door decorations (internal)
Cold Water Plant & Equipment | [8 empty] | LOW | 2 | 2
Cold Water Storage Tanks | [8 empty] | Door decorations (internal) Total | 2 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Paint
Cold Water Storage Tanks Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Cold Water Plant & Equipment Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Paint Total | 2 | 2
Comfort Cooling | [8 empty] | Decorations Total | 2.5571 | 2
Refrigerant pipework systems | [8 empty] | Door
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Solid veneer faced timber door (Single) with vision panel
Refrigerant pipework systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Condensate pipework system | [8 empty] | Solid veneer faced timber door (Single) with vision panel Total | 3 | 2
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Fire door furniture
Condensate pipework system Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | SIGNIFICANT | 4 | 3
Computer room air conditioning | [8 empty] | Fire door furniture Total | 4 | 3
C | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | Door Total | 3.5 | 2.5
Computer room air conditioning Total | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | FF&E
Comfort Cooling Total | 5 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | Blinds
Communication System | [8 empty] | MODERATE | 3 | 2
Television and satellite systems | [8 empty] | Blinds Total | 3 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | FF&E Total | 3 | 2
Television and satellite systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Finishes
Communication systems | [8 empty] | Carpet Tile
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Communication systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Public address systems | [8 empty] | Carpet Tile Total | 2.9062 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Barrier Matting
Public address systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Communication System Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Barrier Matting Total | 3 | 2
Cubicles | [8 empty] | Vinyl tiles
High Pressure Laminated Chipboard | [8 empty] | MODERATE | 3 | 2
C | 4 | 2 | 0 | 5200 | 0 | 0 | 0 | 5200 | LOW | 2 | 2
High Pressure Laminated Chipboard Total | 4 | 2 | 0 | 5200 | 0 | 0 | 0 | 5200 | Vinyl tiles Total | 2.5 | 2
Timber cubicle door | [8 empty] | Raised access tiles
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | SIGNIFICANT | 3 | 4
Timber cubicle door Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Raised access tiles Total | 3 | 4
Cubicles Total | 5 | 3.2 | 0 | 5200 | 0 | 0 | 0 | 5200 | Sheet Vinyl (slip resistant)
Decorations | [8 empty] | MODERATE | 3 | 2.1667
Emulsion paint finish to walls | [8 empty] | Sheet Vinyl (slip resistant) Total | 3 | 2.1667
B | 63 | 7.746 | 0 | 0 | 0 | 0 | 0 | 0 | Carpet Sheet
C | 54 | 2.7037 | 0 | 1506.0222 | 9448.8264 | 371.7 | 0 | 11326.5486 | MODERATE | 3 | 2
A | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Emulsion paint finish to walls Total | 119 | 5.4286 | 0 | 1506.0222 | 9448.8264 | 371.7 | 0 | 11326.5486 | Carpet Sheet Total | 2.5 | 2
Emulsion paint finish to Ceiling | [8 empty] | Vinyl tile (blistered)
C | 1 | 3 | 0 | 0 | 181.02 | 0 | 0 | 181.02 | MODERATE | 3 | 2
Emulsion paint finish to Ceiling Total | 1 | 3 | 0 | 0 | 181.02 | 0 | 0 | 181.02 | Vinyl tile (blistered) Total | 3 | 2
Decoration of timber surfaces | [8 empty] | Sheet Vinyl
C | 2 | 2.5 | 0 | 14 | 35 | 0 | 0 | 49 | MODERATE | 3 | 2
A | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Decoration of timber surfaces Total | 3 | 3.6667 | 0 | 14 | 35 | 0 | 0 | 49 | Sheet Vinyl Total | 2.5 | 2
Joinery decorations (architraves, skirting) | [8 empty] | Timber boarding (raised floor)
B | 16 | 6.625 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 3
C | 10 | 2.8 | 0 | 49 | 168 | 35 | 0 | 252 | Timber boarding (raised floor) Total | 3 | 3
A | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | Floor Finishes Total | 2.8627 | 2.0784
Joinery decorations (architraves, skirting) Total | 28 | 5.2143 | 0 | 49 | 168 | 35 | 0 | 252 | IPS
Timber surround to rooflight | [8 empty] | High Pressure Laminated Chipboard
C | 1 | 2 | 0 | 10 | 0 | 0 | 0 | 10 | MODERATE | 2.7143 | 2.2857
Timber surround to rooflight Total | 1 | 2 | 0 | 10 | 0 | 0 | 0 | 10 | LOW | 2 | 2
Door decorations (internal) | [8 empty] | High Pressure Laminated Chipboard Total | 2.625 | 2.25
B | 3 | 6.6667 | 0 | 0 | 0 | 0 | 0 | 0 | IPS Total | 2.625 | 2.25
C | 1 | 4 | 0 | 0 | 0 | 39.24 | 0 | 39.24 | Ironmongery
Door decorations (internal) Total | 4 | 6 | 0 | 0 | 0 | 39.24 | 0 | 39.24 | Ironmongery (general item)
Floor Paint | [8 empty] | MODERATE | 3 | 2.75
B | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150 | Ironmongery (general item) Total | 2.5714 | 2.4286
Floor Paint Total | 29 | 7.7931 | 0 | 150 | 0 | 0 | 0 | 150 | Door Lever
Decorations Total | 185 | 5.7189 | 0 | 1729.0222 | 9832.8464 | 445.94 | 0 | 12007.8086 | LOW | 2 | 2
Door | [8 empty] | Door Lever Total | 2 | 2
Solid veneer faced timber door (Single) with vision panel | [8 empty] | Lever handle
B | 32 | 10.125 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 1 | 1 | 100 | 0 | 0 | 0 | 0 | 100 | Lever handle Total | 2 | 2
A | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Door closer
Solid veneer faced timber door (Single) with vision panel Total | 37 | 10.9459 | 100 | 0 | 0 | 0 | 0 | 100 | MODERATE | 3 | 2
Solid veneer faced timber door (Single) | [8 empty] | Door closer Total | 3 | 2
B | 50 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | Pull handles
Solid veneer faced timber door (Single) Total | 50 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Solid veneer faced timber door (Double) with vision panel | [8 empty] | Pull handles Total | 2 | 2
B | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | Ironmongery Total | 2.3125 | 2.1875
Solid veneer faced timber door (Double) with vision panel Total | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery
Hollow core door (Single) | [8 empty] | Timber sub frame / sill / general surfaces
B | 8 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Hollow core door (Single) Total | 8 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | Timber sub frame / sill / general surfaces Total | 3 | 2
Fire door furniture | [8 empty] | Ply boxing
D | 1 | 1 | 25 | 0 | 0 | 0 | 0 | 25 | LOW | 2 | 2
Fire door furniture Total | 1 | 1 | 25 | 0 | 0 | 0 | 0 | 25 | Ply boxing Total | 2 | 2
Aluminium fully glazed door | [8 empty] | Joinery Total | 2.5 | 2
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Mechanical Ventilation
Aluminium fully glazed door Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Centrifugal fans
Glazed Double Leaf | [8 empty] | LOW | 2 | 2
B | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Centrifugal fans Total | 2 | 2
Glazed Double Leaf Total | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Humidifier
Solid veneer faced timber door (Single+Half) with vision panel | [8 empty] | LOW | 2 | 2
B | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | Humidifier Total | 2 | 2
Solid veneer faced timber door (Single+Half) with vision panel Total | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | Mechanical Ventilation Total | 2 | 2
Steel security door / cell door | [8 empty] | Sink
B | 15 | 15.3333 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China
A | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Steel security door / cell door Total | 17 | 15.8824 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Hollow Core door single (with vision panel) | [8 empty] | Vitreous China Total | 2.8 | 2
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Stainless Steel
Hollow Core door single (with vision panel) Total | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 3
Door Total | 130 | 11.1077 | 125 | 0 | 0 | 0 | 0 | 125 | Stainless Steel Total | 3 | 3
FF&E | [8 empty] | Sink Total | 2.8333 | 2.1667
Dumb waiter | [8 empty] | Vanity Unit
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | High Pressure Laminated Chipboard
Dumb waiter Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Laminate worktop on metal legs | [8 empty] | LOW | 2 | 2
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | High Pressure Laminated Chipboard Total | 2.8333 | 2
Laminate worktop on metal legs Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Vanity Unit Total | 2.8333 | 2
Blinds | [8 empty] | Wall Finishes
B | 15 | 7.7333 | 0 | 0 | 0 | 0 | 0 | 0 | Plaster on Brick/Block
C | 4 | 2 | 0 | 600 | 0 | 0 | 0 | 600 | MODERATE | 3 | 2
Blinds Total | 19 | 6.5263 | 0 | 600 | 0 | 0 | 0 | 600 | LOW | 2 | 2
Worktop & units | [8 empty] | Plaster on Brick/Block Total | 2.8 | 2
B | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | Hessian wall panels
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Worktop & units Total | 3 | 9.6667 | 0 | 0 | 0 | 0 | 0 | 0 | Hessian wall panels Total | 3 | 2
Metal handrail | [8 empty] | Wall Finishes Total | 2.8125 | 2
B | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | WC
Metal handrail Total | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China
Benches | [8 empty] | MODERATE | 3 | 2
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China Total | 3 | 2
Benches Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | WC Total | 3 | 2
Built in cupboards etc | [8 empty] | Grand Total | 2.6783 | 2.0478
B | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Built in cupboards etc Total | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Timber staircase
B | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Timber staircase Total | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Shelfing
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Shelfing Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Laminated reception desk
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Laminated reception desk Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Reception glazing (aluminium framed)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Reception glazing (aluminium framed) Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted fixed timber seating with metal frame
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted fixed timber seating with metal frame Total | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Vertical
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Vertical Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Drop down
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Drop down Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Hand Rails
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Hand Rails Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Units
B | 3 | 9.3333 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Units Total | 4 | 10.75 | 0 | 0 | 0 | 0 | 0 | 0
Benching
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Benching Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fixed laminate Worktop / desking
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fixed laminate Worktop / desking Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen units with laminate worktops
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen units with laminate worktops Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fixed base timber units
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fixed base timber units Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted seat and counter
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted seat and counter Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fixed wooden bed (vandalised wooden tops)
B | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fixed wooden bed (vandalised wooden tops) Total | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Dumbwaiter lift
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Dumbwaiter lift Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
FF&E Total | 68 | 9.6029 | 0 | 600 | 0 | 0 | 0 | 600
Floor Finishes
Carpet Tile
B | 25 | 8.32 | 0 | 0 | 0 | 0 | 0 | 0
C | 32 | 2.8438 | 0 | 6422.8204 | 32305.4182 | 0 | 522.96 | 39251.1986
Carpet Tile Total | 57 | 5.2456 | 0 | 6422.8204 | 32305.4182 | 0 | 522.96 | 39251.1986
Barrier Matting
C | 2 | 3 | 0 | 0 | 430.26 | 0 | 0 | 430.26
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Barrier Matting Total | 3 | 8.6667 | 0 | 0 | 430.26 | 0 | 0 | 430.26
Vinyl tiles
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 2 | 3 | 0 | 0 | 328.831 | 0 | 0 | 328.831
Vinyl tiles Total | 3 | 4.6667 | 0 | 0 | 328.831 | 0 | 0 | 328.831
Raised access tiles
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 1 | 30 | 0 | 0 | 0 | 0 | 30
Raised access tiles Total | 3 | 5.6667 | 30 | 0 | 0 | 0 | 0 | 30
Quarry Tiles
B | 9 | 8.8889 | 0 | 0 | 0 | 0 | 0 | 0
Quarry Tiles Total | 9 | 8.8889 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl (slip resistant)
B | 9 | 8.2222 | 0 | 0 | 0 | 0 | 0 | 0
C | 6 | 1.6667 | 440.684 | 2639.058 | 0 | 0 | 0 | 3079.742
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl (slip resistant) Total | 16 | 6.1875 | 440.684 | 2639.058 | 0 | 0 | 0 | 3079.742
Carpet Sheet
C | 2 | 3 | 0 | 0 | 878.3016 | 0 | 0 | 878.3016
Carpet Sheet Total | 2 | 3 | 0 | 0 | 878.3016 | 0 | 0 | 878.3016
Vinyl tile (blistered)
C | 1 | 3 | 0 | 0 | 260 | 0 | 0 | 260
Vinyl tile (blistered) Total | 1 | 3 | 0 | 0 | 260 | 0 | 0 | 260
Ceramic tiles
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Ceramic tiles Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl
C | 4 | 2.5 | 0 | 336.105 | 1059.8511 | 0 | 0 | 1395.9561
A | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl Total | 5 | 4 | 0 | 336.105 | 1059.8511 | 0 | 0 | 1395.9561
Concrete
B | 28 | 45.8929 | 0 | 0 | 0 | 0 | 0 | 0
A | 13 | 51.9231 | 0 | 0 | 0 | 0 | 0 | 0
Concrete Total | 41 | 47.8049 | 0 | 0 | 0 | 0 | 0 | 0
Timber boarding (raised floor)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 2 | 0 | 100 | 0 | 0 | 0 | 100
Timber boarding (raised floor) Total | 2 | 7 | 0 | 100 | 0 | 0 | 0 | 100
Floor Finishes Total | 143 | 17.8182 | 470.684 | 9497.9834 | 35262.6619 | 0 | 522.96 | 45754.2893
Fuel Services
Gas distribution pipework
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas distribution pipework Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel shut-off valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel shut-off valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel storage tank.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel storage tank. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Services Total | 4 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Controls
Control Panels
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Control Panels Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Control Valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Control Valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Controls Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution
Heating Distribution Pipework
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution Pipework Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Services thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Services thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Plant Manual Isolation Valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Plant Manual Isolation Valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Actuators
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Actuators Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Radiators.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Radiators. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fan Convectors
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fan Convectors Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Natural Convectors
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Natural Convectors Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LTHW Warm air heaters
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LTHW Warm air heaters Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electric Heaters.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electric Heaters. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution Total | 11 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Plant & Auxiliaries
Gas fired boiler 100kw - 300kw
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired boiler 100kw - 300kw Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Flue Systems (stainless steel 200 kw boiler)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Flue Systems (stainless steel 200 kw boiler) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Commercial Circulating Pump (Single or dual type)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Commercial Circulating Pump (Single or dual type) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Air-to-air commercial Heat pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Air-to-air commercial Heat pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Plant & Auxiliaries Total | 4 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Distribution Services
Hot and Cold Water Pipework systems
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot and Cold Water Pipework systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Services thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Services thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Shower mixer and head
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Shower mixer and head Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Distribution Services Total | 6 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Plant & Equipment
Circulating Pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Circulating Pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired hot water heaters
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired hot water heaters Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Boilers - (tea points)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Boilers - (tea points) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Plant & Equipment Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Internal glazing
Softwood Timber
B | 7 | 8.5714 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber Total | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Metal frame
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Metal frame Total | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0
Softwood timber (veneer)
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Softwood timber (veneer) Total | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Rooflight with metal frame
B | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Rooflight with metal frame Total | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber (painted)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber (painted) Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Internal glazing Total | 26 | 10.9231 | 0 | 0 | 0 | 0 | 0 | 0
IPS
High Pressure Laminated Chipboard
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 8 | 2 | 0 | 7150 | 0 | 0 | 0 | 7150
High Pressure Laminated Chipboard Total | 10 | 3.2 | 0 | 7150 | 0 | 0 | 0 | 7150
IPS Total | 10 | 3.2 | 0 | 7150 | 0 | 0 | 0 | 7150
Ironmongery
Ironmongery (general item)
B | 101 | 10.3366 | 0 | 0 | 0 | 0 | 0 | 0
C | 7 | 2.4286 | 0 | 475 | 205 | 0 | 0 | 680
A | 4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0
Ironmongery (general item) Total | 112 | 10.0982 | 0 | 475 | 205 | 0 | 0 | 680
Door Lever
C | 2 | 2 | 0 | 50 | 0 | 0 | 0 | 50
Door Lever Total | 2 | 2 | 0 | 50 | 0 | 0 | 0 | 50
Lever handle
C | 5 | 2 | 0 | 125 | 0 | 0 | 0 | 125
Lever handle Total | 5 | 2 | 0 | 125 | 0 | 0 | 0 | 125
Door closer
C | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Door closer Total | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Pull handles
C | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Pull handles Total | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Ironmongery Total | 121 | 9.4959 | 0 | 700 | 205 | 0 | 0 | 905
Joinery
Timber skirting
B | 65 | 8.5538 | 0 | 0 | 0 | 0 | 0 | 0
A | 4 | 15.75 | 0 | 0 | 0 | 0 | 0 | 0
Timber skirting Total | 69 | 8.971 | 0 | 0 | 0 | 0 | 0 | 0
Timber dado / picture rail
B | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber dado / picture rail Total | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber / MDF architraves
B | 93 | 9.8495 | 0 | 0 | 0 | 0 | 0 | 0
A | 4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0
Timber / MDF architraves Total | 97 | 10.1649 | 0 | 0 | 0 | 0 | 0 | 0
Timber sub frame / sill / general surfaces
B | 24 | 8.1667 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 3 | 0 | 0 | 50 | 0 | 0 | 50
Timber sub frame / sill / general surfaces Total | 25 | 7.96 | 0 | 0 | 50 | 0 | 0 | 50
Ply boxing
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Ply boxing Total | 2 | 6 | 0 | 150 | 0 | 0 | 0 | 150
Timber deck
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber deck Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
MDF / Ply panels above window
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
MDF / Ply panels above window Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Panelling to radiator
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Panelling to radiator Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber surround to rooflight
B | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber surround to rooflight Total | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Metal joinery
B | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Metal joinery Total | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Joinery Total | 222 | 9.2613 | 0 | 150 | 50 | 0 | 0 | 200
Lifting Equipment
Lift Plant & Controls
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lift Plant & Controls Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lifting Equipment Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting Systems
Emergency lighting (inc key switch)
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Emergency lighting (inc key switch) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (internal)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (internal) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (external)
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (external) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting Systems Total | 7 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mains Power Supplies
LV switchgear (internal)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LV switchgear (internal) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Main supply switchgear
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Main supply switchgear Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
SWA mains/sub distribution cables.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
SWA mains/sub distribution cables. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Earth bonding (Primary)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Earth bonding (Primary) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electricity Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electricity Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mains Power Supplies Total | 5 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Ventilation
Packaged Air handling units
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Packaged Air handling units Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Galvanised Ductwork Systems
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Galvanised Ductwork Systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Centrifugal fans
C | 1 | 5 | 0 | 0 | 0 | 0 | 1000 | 1000
Centrifugal fans Total | 1 | 5 | 0 | 0 | 0 | 0 | 1000 | 1000
Ductwork thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Ductwork thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
External louvres steel painted
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
External louvres steel painted Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Humidifier
C | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000
Humidifier Total | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000
Kitchen Extract canopies/ Hoods (average)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Extract canopies/ Hoods (average) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Local extract fans
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Local extract fans Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fire Dampers
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fire Dampers Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Grilles and diffusers
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Grilles and diffusers Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Ventilation Total | 13 | 3 | 10000 | 0 | 0 | 0 | 1000 | 11000
Miscellaneous Electrical Equipment & Plant
Kitchen (cooking and support systems)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Kitchen (cooking and support systems) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Electrical Equipment & Plant Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Mechanical Equipment & Plant
Petrol & Diesel Storage and Pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Petrol & Diesel Storage and Pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Mechanical Equipment & Plant Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Other
Showers
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Showers Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Metal shower
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Metal shower Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Other Total | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Power Generation
Standby generator plus prime mover
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Standby generator plus prime mover Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Power Generation Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sink
Cleaners sink (Belfast etc)
B | 4 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0
Cleaners sink (Belfast etc) Total | 4 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0
Vitreous China
B | 7 | 8.2857 | 0 | 0 | 0 | 0 | 0 | 0
C | 5 | 2 | 0 | 3761.42 | 0 | 0 | 0 | 3761.42
Vitreous China Total | 12 | 5.6667 | 0 | 3761.42 | 0 | 0 | 0 | 3761.42
Stainless Steel
B | 3 | 9.3333 | 0 | 0 | 0 | 0 | 0 | 0
D | 1 | 1 | 100 | 0 | 0 | 0 | 0 | 100
Stainless Steel Total | 4 | 7.25 | 100 | 0 | 0 | 0 | 0 | 100
Sink Total | 20 | 7.1 | 100 | 3761.42 | 0 | 0 | 0 | 3861.42
Sub-Main Distribution
Sub distribution wiring and containment systems
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sub distribution wiring and containment systems Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fixed appliance power supplies/ isolators (Spurs)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fixed appliance power supplies/ isolators (Spurs) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (critical)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (critical) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (Non critical)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (Non critical) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Switched socket outlet (SSO)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Switched socket outlet (SSO) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sub-Main Distribution Total | 9 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Urinal
Vitreous China
B | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Vitreous China Total | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Urinal Total | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Vanity Unit
High Pressure Laminated Chipboard
B | 3 | 7.3333 | 0 | 0 | 0 | 0 | 0 | 0
C | 6 | 2 | 0 | 3900 | 0 | 0 | 0 | 3900
High Pressure Laminated Chipboard Total | 9 | 3.7778 | 0 | 3900 | 0 | 0 | 0 | 3900
Vanity Unit Total | 9 | 3.7778 | 0 | 3900 | 0 | 0 | 0 | 3900
Wall Finishes
Plaster on Brick/Block
B | 107 | 12.1402 | 0 | 0 | 0 | 0 | 0 | 0
C | 15 | 2.2 | 0 | 622.688 | 406.87 | 0 | 0 | 1029.558
A | 4 | 25 | 0 | 0 | 0 | 0 | 0 | 0
Plaster on Brick/Block Total | 126 | 11.3651 | 0 | 622.688 | 406.87 | 0 | 0 | 1029.558
Ceramic Wall Tiles
B | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 0
Ceramic Wall Tiles Total | 14 | 14.5714 | 0 | 0 | 0 | 0 | 0 | 0
Metal / timber stud with plasterboard
B | 4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0
Metal / timber stud with plasterboard Total | 4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0
Pre-finished panels
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Pre-finished panels Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Exposed Concrete
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
A | 7 | 57.8571 | 0 | 0 | 0 | 0 | 0 | 0
Exposed Concrete Total | 9 | 46.7778 | 0 | 0 | 0 | 0 | 0 | 0
Brickwork
B | 18 | 40 | 0 | 0 | 0 | 0 | 0 | 0
A | 15 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Brickwork Total | 33 | 46.8182 | 0 | 0 | 0 | 0 | 0 | 0
Hessian wall panels
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Hessian wall panels Total | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Glazed partitions
B | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Glazed partitions Total | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Acoustic Wall Panels
B | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Acoustic Wall Panels Total | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Metal wall panels
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Metal wall panels Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Blockwork
A | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Blockwork Total | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Wall Finishes Total | 196 | 19.9235 | 0 | 772.688 | 406.87 | 0 | 0 | 1179.558
WC
Vitreous China
B | 25 | 8.64 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 3 | 0 | 0 | 615.82 | 0 | 0 | 615.82
Vitreous China Total | 26 | 8.4231 | 0 | 0 | 615.82 | 0 | 0 | 615.82
WC Total | 26 | 8.4231 | 0 | 0 | 615.82 | 0 | 0 | 615.82
#N/A
#N/A
(blank) |  |  | 0 | 0 | 0 | 0 | 0 | 0
#N/A Total |  |  | 0 | 0 | 0 | 0 | 0 | 0
#N/A Total |  |  | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 1390 | 11.7188 | 20695.684 | 59822.0295 | 62978.0169 | 445.94 | 1522.96 | 145464.6304
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Fabric Survey
Condition Ranking | [9 empty] | Priority |  |  | Type
A |  |  | A = Good - Performing as intended and operating efficiently | [6 empty] | 1 | Urgent |  | E | Environmental
B |  |  | B = Satisfactory - performing as intended, exhibiting minor deterioration. | [6 empty] | 2 | within 2 years |  | F | Fire Precaution
C |  |  | C = Poor - exhibiting major defects and/or not operating as intended. | [6 empty] | 3 | 3 to 5 years |  | G | Consequential risk
D |  |  | D = Failed - life expired and/or serious risk imminent failure | [6 empty] | 4 | 5 to 10 years |  | H | Health and Safety
[10 empty] | 5 | 10 to 15 years |  | I | Further Investigation
[10 empty] | 6 | 15 to 25 years |  | L | Loss of Service
[13 empty] | Q | Energy
[13 empty] | R | Recommendation
[13 empty] | S | Security
ROOM DESCRIPTION |  |  |  | ROOM FABRIC | [5 empty] | CONDITION SURVEY
Internal / External | Building | Room No. / Name | Floor | Element | Element | Element group | Element group | Sub element group | Sub element group | Unit rate | Item quantity | Standard Rate | CONDITION RANK | PRIORITY | TYPE | Typical Life from new (YEARS) | Estimated Remaining Useful Design Life (YEARS) | Cost | Disrepair Narrative / General Comments | Remedial Works | Photo ref: (Applied to "C" or "D" ratings i.e.. Cx or Dx) | Current & Impending Backlog Risk Assessment |  | SCORE RANGE | RISK RANKING | PREDICTED REPLACEMENT (£1s) | [5 empty] | Total | General Comments
[24 empty] | 1 - 5 | Low | 1 | 1-2 | 3-5 | 5-10 | 10-15 | 15-25 |  | Remedial Works
[21 empty] | Photo ref: (Applied to "C" or "D" ratings i.e.. Cx or Dx) | #REF! | #REF! | SCORE RANGE | RISK RANKING | Priority 1 - 2018/19 | Priority 2 - 2019/20 | Priority 3 - 2020/23 | Priority 4 - 2023/28 | Priority 5 - 2028/33 | Priority 6 - 2033/42 |  | General Comments
External Areas | 1 | External | 0 |  | Fencing | Fencing & Gates | Fencing & Security |  | Timber boards | m | 20 | 106.5 | D | 1 | F | 15 | Urgent | 2130 | Timber fencing and gates to secure rear and sides of property do not have furniture suitable to allow fire egress. | Renew for new fencing and gates with escape facility. | N/A |  |  |  |  | 2130 | [5 empty] | 2130
External Areas | 1 | External | 0 |  | Fencing | Fencing & Gates | Fencing & Security |  | Timber boards | m | 20 | 106.5 | A | 6 | F | 15 | 15-25 years | 2130 | Timber fencing and gates to secure rear and sides of property do not have furniture suitable to allow fire egress. | Renew for new fencing and gates with escape facility. | N/A | [9 empty] | 2130 | 2130
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Tarmacadam | m2 | 30 | 120 | B | 2 | R | 20 | Within 2 years | 3600 | Foot paths too narrow to allow wheelchairs or persons with mobility aids o pass. | Form passing places along footpaths to allow occupants to pass without moving on to grassed areas. | N/A | [5 empty] | 3600 |  |  |  |  | 3600
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Tarmacadam | m2 | 100 | 120 | B | 2 | R | 20 | Within 2 years | 12000 | Utilise more of the external grounds to extend the recreational seating areas, avoid gravel and uneven surfaces. | Refurbish external seating areas. | N/A | [5 empty] | 12000 |  |  |  |  | 12000
External Areas | 1 | External | 0 |  | Ramps & Steps | Fencing & Gates | Ramp |  | Ramps to exit doors | Ea | 12 | 850 | C | 2 | H | 20 | Within 2 years | 10200 | Brick ramps steep and potential to be slippery when wet, concrete ramps steep inadequate handrails | Allow to remove external sloped ramps to exit doors from building. Install new concrete ramps with landing and handrails | N/A | [5 empty] | 10200 |  |  |  |  | 10200
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roofs - pitched |  | Concrete tiles | m2 | 1195 | 143 | B | 4 | G | 40 | 5-10 years | 170885 | Existing concrete interlocking tiles appears weatherproof but now nearing the end of useable life | Allow to remove and refit concrete interlocking tiles to pitched roofs and renew including new insulation. | N/A | [7 empty] | 170885 |  |  | 170885
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roofs - flat |  | Mineral felt | m2 | 475 | 160 | C | 2 | G | 20 | Within 2 years | 76000 | Existing covering is felt with polystyrene tiles and chippings on top, aged and deteriorating many patch repairs evident. | Remove then allow for cut to falls insulation and mineral felt covering. | N/A | [5 empty] | 76000 |  |  |  |  | 76000
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roofs - flat |  | Mineral felt | m2 | 475 | 160 | A | 6 | R | 20 | 15-25 years | 76000 | Renewal of replacement covering | Renew to the building regulations | N/A | [9 empty] | 76000 | 76000
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roof Drainage |  | Concrete gutters | m | 160 | 60 | C | 2 | G | 25 | Within 2 years | 9600 | Gutters to mono pitched roofs are concrete sectional box gutters. Have been relined with felt as a retrospective repair, some leaking evident. | Reline with a cold applied liquid gutter lining system e.g Sika | N/A | [5 empty] | 9600 |  |  |  |  | 9600
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roof lights |  | Propriety Unit | Nr | 20 | 1107 | C | 2 | G | 25 | Within 2 years | 22140 | Aged polycarbonate rooflights. | Renew in conjunction with roof recover | N/A | [5 empty] | 22140 |  |  |  |  | 22140
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Windows |  | PVCu windows | m2 | 167 | 767 | B | 5 | G | 35 | 10-15 years | 128089 | Existing windows throughout the site are PVCu double glazed, UV fading and weathering evident. | Replace | N/A | [8 empty] | 128089 |  | 128089
1 | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Doors |  | PVCu Doors | Nr | 12 | 1279 | B | 5 | S | 30 | 10-15 years | 15348 | Existing PVCu throughout the site are PVCu double glazed, UV fading and weathering evident. | Recommend replacement with powder coated aluminium for durability | N/A | [8 empty] | 15348 |  | 15348
External | 2 | External | 1 |  | Building Superstructure | Fencing & Gates | Doors |  | PVCu Doors | Nr | 1 | 3821 | C | 2 | S | 30 | Within 2 years | 3821 | The main entrance PVCu double doorset is not powered, has access control and slightly raised threshold, which combined with the double doorsets may pose awkward for ambulance crews. | Recommend replacement with powder coated aluminium for durability | N/A | [5 empty] | 3821 |  |  |  |  | 3821
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 225 | 11 | B | 3 | E | 5 | 3-5 years | 2475 | Generally good condition | Redecorate | N/A | [6 empty] | 2475 |  |  |  | 2475
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 225 | 11 | A | 4 | E | 5 | 5-10 years | 2475 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 2475 |  |  | 2475
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 225 | 11 | A | 5 | E | 5 | 10-15 years | 2475 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 2475 |  | 2475
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 225 | 11 | A | 6 | E | 5 | 15-25 years | 2475 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 2475 | 2475
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 225 | 11 | A | 6 | E | 5 | 15-25 years | 2475 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 2475 | 2475
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 475 | 11.29 | B | 3 | E | 5 | 3-5 years | 5362.75 | Generally good condition | Redecorate | N/A | [6 empty] | 5362.75 |  |  |  | 5362.75
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 475 | 11.29 | A | 4 | E | 5 | 5-10 years | 5362.75 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 5362.75 |  |  | 5362.75
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 475 | 11.29 | A | 5 | E | 5 | 10-15 years | 5362.75 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 5362.75 |  | 5362.75
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 475 | 11.29 | A | 6 | E | 5 | 15-25 years | 5362.75 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 5362.75 | 5362.75
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 475 | 11.29 | A | 6 | E | 5 | 15-25 years | 5362.75 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 5362.75 | 5362.75
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet tile | m2 | 225 | 59 | B | 4 | E | 15 | 5-10 years | 13275 | Generally good condition | Replace | N/A | [7 empty] | 13275 |  |  | 13275
A | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet tile | m2 | 225 | 59 | A | 6 | E | 15 | 15-25 years | 13275 | Cyclical replacement | Replace | N/A | [9 empty] | 13275 | 13275
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 356 | 11 | B | 3 | E | 5 | 3-5 years | 3916 | Generally good condition | Redecorate | N/A | [6 empty] | 3916 |  |  |  | 3916
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 356 | 11 | A | 4 | E | 5 | 5-10 years | 3916 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 3916 |  |  | 3916
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 356 | 11 | A | 5 | E | 5 | 10-15 years | 3916 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 3916 |  | 3916
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 356 | 11 | A | 6 | E | 5 | 15-25 years | 3916 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 3916 | 3916
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 356 | 11 | A | 6 | E | 5 | 15-25 years | 3916 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 3916 | 3916
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 912 | 11.29 | B | 3 | E | 5 | 3-5 years | 10296.48 | Generally good condition | Redecorate | N/A | [6 empty] | 10296.48 |  |  |  | 10296.48
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 912 | 11.29 | A | 4 | E | 5 | 5-10 years | 10296.48 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 10296.48 |  |  | 10296.48
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 912 | 11.29 | A | 5 | E | 5 | 10-15 years | 10296.48 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 10296.48 |  | 10296.48
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 912 | 11.29 | A | 6 | E | 5 | 15-25 years | 10296.48 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 10296.48 | 10296.48
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 912 | 11.29 | A | 6 | E | 5 | 15-25 years | 10296.48 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 10296.48 | 10296.48
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Floor finishes |  | Carpet tile | m2 | 356 | 59 | B | 4 | E | 15 | 5-10 years | 21004 | Generally good condition | Replace | N/A | [7 empty] | 21004 |  |  | 21004
A | 1 | Circulation Areas | 0 |  | Internal finishes |  | Floor finishes |  | Carpet tile | m2 | 356 | 59 | A | 6 | E | 15 | 15-25 years | 21004 | Cyclical replacement | Replace | N/A | [9 empty] | 21004 | 21004
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | B | 3 | H | 5 | 3-5 years | 264 | Generally good condition | Redecorate | N/A | [6 empty] | 264 |  |  |  | 264
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 4 | E | 5 | 5-10 years | 264 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 264 |  |  | 264
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 5 | E | 5 | 10-15 years | 264 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 264 |  | 264
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 6 | E | 5 | 15-25 years | 264 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 264 | 264
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 6 | E | 5 | 15-25 years | 264 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 264 | 264
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | B | 3 | H | 5 | 3-5 years | 836 | Generally good condition | Redecorate | N/A | [6 empty] | 836 |  |  |  | 836
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 4 | E | 5 | 5-10 years | 836 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 836 |  |  | 836
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 5 | E | 5 | 10-15 years | 836 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 836 |  | 836
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 6 | E | 5 | 15-25 years | 836 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 836 | 836
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 6 | E | 5 | 15-25 years | 836 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 836 | 836
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 24 | 95 | B | 4 | H | 15 | 5-10 years | 2280 | Generally good condition | Replace | N/A | [7 empty] | 2280 |  |  | 2280
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 24 | 95 | A | 6 | E | 15 | 15-25 years | 2280 | Cyclical replacement | Replace | N/A | [9 empty] | 2280 | 2280
Internal | 1 | Kitchen / Kitchenettes | 0 |  | FF&E | FF&E | FF&E |  | Worktop & Units | Item | 1 | 4250 | B | 5 | H | 15 | 10-15 years | 4250 | Good condition | Replace | N/A | [8 empty] | 4250 |  | 4250
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 4 | 931 | B | 5 | H | 25 | 10-15 years | 3724 | Generally good condition | Replace | N/A | [8 empty] | 3724 |  | 3724
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | B | 3 | H | 5 | 3-5 years | 264 | Generally good condition | Redecorate | N/A | [6 empty] | 264 |  |  |  | 264
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 4 | E | 5 | 5-10 years | 264 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 264 |  |  | 264
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 5 | E | 5 | 10-15 years | 264 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 264 |  | 264
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 6 | E | 5 | 15-25 years | 264 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 264 | 264
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 24 | 11 | A | 6 | E | 5 | 15-25 years | 264 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 264 | 264
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | B | 3 | H | 5 | 3-5 years | 836 | Generally good condition | Redecorate | N/A | [6 empty] | 836 |  |  |  | 836
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 4 | E | 5 | 5-10 years | 836 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 836 |  |  | 836
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 5 | E | 5 | 10-15 years | 836 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 836 |  | 836
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 6 | E | 5 | 15-25 years | 836 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 836 | 836
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 76 | 11 | A | 6 | E | 5 | 15-25 years | 836 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 836 | 836
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 24 | 95 | B | 3 | H | 10 | 3-5 years | 2280 | Generally good condition | Replace | N/A | [6 empty] | 2280 |  |  |  | 2280
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 24 | 95 | A | 6 | E | 15 | 15-25 years | 2280 | Cyclical replacement | Replace | N/A | [9 empty] | 2280 | 2280
Internal | 1 | Toilets | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) | Item | 4 | 391 | B | 5 | H | 25 | 10-15 years | 1564 | Generally good condition | Replace | N/A | [8 empty] | 1564 |  | 1564
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | B | 3 | H | 5 | 3-5 years | 440 | Generally good condition | Replace | N/A | [6 empty] | 440 |  |  |  | 440
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 4 | E | 5 | 5-10 years | 440 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 440 |  |  | 440
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 5 | E | 5 | 10-15 years | 440 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 440 |  | 440
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 6 | E | 5 | 15-25 years | 440 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 440 | 440
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 6 | E | 5 | 15-25 years | 440 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 440 | 440
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Ceramic tiles to walls | m2 | 96 | 234 | B | 3 | H | 5 | 3-5 years | 22464 | Generally fair condition, aging | Currently paint to walls, install ceramic tiles for hygiene and durability | N/A | [6 empty] | 22464 |  |  |  | 22464
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 40 | 95 | B | 3 | H | 10 | 3-5 years | 3800 | Generally fair condition | Replace | N/A | [6 empty] | 3800 |  |  |  | 3800
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 40 | 95 | A | 6 | E | 15 | 15-25 years | 3800 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 3800 | 3800
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | WHB |  | Vitreous China | Item | 6 | 525 | B | 3 | H | 20 | 3-5 years | 3150 | In 6nr bathrooms - Generally fair condition | Replace | N/A | [6 empty] | 3150 |  |  |  | 3150
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | WHB |  | Vitreous China | Item | 6 | 525 | A | 6 | H | 20 | 15-25 years | 3150 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 3150 | 3150
Internal | 1 | Bath / shower rooms | 1 |  | Sanitaryware | FF&E | WC |  | Vitreous China | Item | 6 | 525 | B | 5 | H | 20 | 10-15 years | 3150 | In 1nr bathrooms - Good condition | Replace | N/A | [8 empty] | 3150 |  | 3150
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | Bath |  | Height adjustable bath | Item | 5 | 7500 | B | 3 | H | 15 | 3-5 years | 37500 | Rise and fall height adjustable bath. Fair condition, aging | Replace | N/A | [6 empty] | 37500 |  |  |  | 37500
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | Bath |  | Height adjustable bath | Item | 5 | 7500 | A | 6 | H | 15 | 15-25 years | 37500 | Rise and fall height adjustable bath. Fair condition, aging | Cyclical replacement | N/A | [9 empty] | 37500 | 37500
Internal | 2 | Bath / shower rooms | 1 |  | Sanitaryware | FF&E | Bath |  | Height adjustable bath | Item | 1 | 7500 | B | 5 | H | 15 | 10-15 years | 7500 | Rise and fall height adjustable bath. Good condition | Replace | N/A | [8 empty] | 7500 |  | 7500
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | Shower |  | Shower cubicle | Item | 1 | 3500 | B | 4 | H | 10 | 5-10 years | 3500 | Good condition | Replace | N/A | [7 empty] | 3500 |  |  | 3500
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | Shower |  | Shower cubicle | Item | 1 | 3500 | A | 6 | H | 10 | 5-10 years | 3500 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 3500 | 3500
Internal | 1 | Bath / shower rooms | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) | Item | 7 | 391 | B | 3 | H | 25 | 3-5 years | 2737 | Appears generally good condition. Bathroom doors do not have own distinguishing colour. | Replace | N/A | [6 empty] | 2737 |  |  |  | 2737
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 25 | 11 | B | 3 | H | 5 | 3-5 years | 275 | Generally good condition | Redecorate | N/A | [6 empty] | 275 |  |  |  | 275
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 25 | 11 | A | 4 | E | 5 | 5-10 years | 275 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 275 |  |  | 275
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 25 | 11 | A | 5 | E | 5 | 10-15 years | 275 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 275 |  | 275
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 25 | 11 | A | 6 | E | 5 | 15-25 years | 275 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 275 | 275
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 25 | 11 | A | 6 | E | 5 | 15-25 years | 275 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 275 | 275
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 122 | 11 | B | 3 | H | 5 | 3-5 years | 1342 | Generally good condition | Redecorate | N/A | [6 empty] | 1342 |  |  |  | 1342
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 122 | 11 | A | 4 | E | 5 | 5-10 years | 1342 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 1342 |  |  | 1342
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 122 | 11 | A | 5 | E | 5 | 10-15 years | 1342 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 1342 |  | 1342
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 122 | 11 | A | 6 | E | 5 | 15-25 years | 1342 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 1342 | 1342
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 122 | 11 | A | 6 | E | 5 | 15-25 years | 1342 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 1342 | 1342
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 25 | 95 | B | 3 | H | 10 | 3-5 years | 2375 | Generally good condition | Replace | N/A | [6 empty] | 2375 |  |  |  | 2375
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 25 | 95 | A | 6 | H | 10 | 15-25 years | 2375 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 2375 | 2375
Internal | 1 | Laundry | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 1 | 931 | B | 5 | H | 25 | 10-15 years | 931 | Generally good condition | Replace | N/A | [8 empty] | 931 |  | 931
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 27 | 11 | B | 3 | H | 5 | 3-5 years | 297 | Generally good condition | Redecorate | N/A | [6 empty] | 297 |  |  |  | 297
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 27 | 11 | A | 4 | E | 5 | 5-10 years | 297 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 297 |  |  | 297
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 27 | 11 | A | 5 | E | 5 | 10-15 years | 297 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 297 |  | 297
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 27 | 11 | A | 6 | E | 5 | 15-25 years | 297 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 297 | 297
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 27 | 11 | A | 6 | E | 5 | 15-25 years | 297 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 297 | 297
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 128 | 11 | B | 3 | H | 5 | 3-5 years | 1408 | Generally good condition | Redecorate | N/A | [6 empty] | 1408 |  |  |  | 1408
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 128 | 11 | A | 4 | E | 5 | 5-10 years | 1408 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 1408 |  |  | 1408
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 128 | 11 | A | 5 | E | 5 | 10-15 years | 1408 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 1408 |  | 1408
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 128 | 11 | A | 6 | E | 5 | 15-25 years | 1408 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 1408 | 1408
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 128 | 11 | A | 6 | E | 5 | 15-25 years | 1408 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 1408 | 1408
Internal | 1 | Office | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 27 | 95 | B | 3 | H | 10 | 3-5 years | 2565 | Generally fair condition | Replace | N/A | [6 empty] | 2565 |  |  |  | 2565
Internal | 1 | Office | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 27 | 95 | A | 6 | H | 10 | 15-25 years | 2565 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 2565 | 2565
Internal | 1 | Office | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 2 | 931 | B | 5 | H | 25 | 10-15 years | 1862 | Generally good condition | Replace | N/A | [8 empty] | 1862 |  | 1862
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 353 | 11 | B | 3 | H | 5 | 3-5 years | 3883 | Generally good condition | Redecorate | N/A | [6 empty] | 3883 |  |  |  | 3883
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 353 | 11 | A | 4 | E | 5 | 5-10 years | 3883 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 3883 |  |  | 3883
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 353 | 11 | A | 5 | E | 5 | 10-15 years | 3883 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 3883 |  | 3883
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 353 | 11 | A | 6 | E | 5 | 15-25 years | 3883 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 3883 | 3883
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 353 | 11 | A | 6 | E | 5 | 15-25 years | 3883 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 3883 | 3883
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 1150 | 11 | B | 3 | H | 5 | 3-5 years | 12650 | Generally good condition | Redecorate | N/A | [6 empty] | 12650 |  |  |  | 12650
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 1150 | 11 | A | 4 | E | 5 | 5-10 years | 12650 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 12650 |  |  | 12650
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 1150 | 11 | A | 5 | E | 5 | 10-15 years | 12650 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 12650 |  | 12650
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 1150 | 11 | A | 6 | E | 5 | 15-25 years | 12650 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 12650 | 12650
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 1150 | 11 | A | 6 | E | 5 | 15-25 years | 12650 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 12650 | 12650
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 353 | 59 | B | 3 | H | 10 | 3-5 years | 20827 | Generally fair condition | Replace | N/A | [6 empty] | 20827 |  |  |  | 20827
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 353 | 59 | A | 6 | H | 10 | 15-25 years | 20827 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 20827 | 20827
Internal | 1 | Bedrooms | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 40 | 823 | B | 5 | H | 25 | 10-15 years | 32920 | Generally good condition | Replace | N/A | [8 empty] | 32920 |  | 32920
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 54 | 11 | B | 3 | H | 5 | 3-5 years | 594 | Generally good condition | Redecorate | N/A | [6 empty] | 594 |  |  |  | 594
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 54 | 11 | A | 4 | E | 5 | 5-10 years | 594 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 594 |  |  | 594
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 54 | 11 | A | 5 | E | 5 | 10-15 years | 594 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 594 |  | 594
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 54 | 11 | A | 6 | E | 5 | 15-25 years | 594 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 594 | 594
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 54 | 11 | A | 6 | E | 5 | 15-25 years | 594 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 594 | 594
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 165 | 11 | B | 3 | H | 5 | 3-5 years | 1815 | Generally good condition | Redecorate | N/A | [6 empty] | 1815 |  |  |  | 1815
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 165 | 11 | A | 4 | E | 5 | 5-10 years | 1815 | Cyclical redecorations | Redecorate | N/A | [7 empty] | 1815 |  |  | 1815
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 165 | 11 | A | 5 | E | 5 | 10-15 years | 1815 | Cyclical redecorations | Redecorate | N/A | [8 empty] | 1815 |  | 1815
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 165 | 11 | A | 6 | E | 5 | 15-25 years | 1815 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 1815 | 1815
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 165 | 11 | A | 6 | E | 5 | 15-25 years | 1815 | Cyclical redecorations | Redecorate | N/A | [9 empty] | 1815 | 1815
Internal | 1 | Storage | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 54 | 95 | B | 3 | H | 10 | 3-5 years | 5130 | Generally fair condition | Replace | N/A | [6 empty] | 5130 |  |  |  | 5130
Internal | 1 | Storage | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 12 | 931 | B | 5 | H | 25 | 10-15 years | 11172 | Generally good condition | Replace | N/A | [8 empty] | 11172 |  | 11172
Internal | 1 | Laundry | G |  | Electrical Services |  | Sub-mains switchgear |  | Distribution Boards | Unit rate | 1 | 1000 | C | 2 | R | 25 | within 2 years | 1000 | Existing distribution boards to the Laundry to be replaced as panel is obsolete. | Replace the existing distribution boards with modern Schneider Acti9 distribution boards to match the ones already replaced. | N/A | [5 empty] | 1000 |  |  |  |  | 1000
Internal | 1 | Flats | 1 |  | Electrical Services |  | Sub-mains switchgear |  | Distribution Boards | Unit rate | 1 | 1000 | C | 2 | R | 25 | within 2 years | 1000 | The flat distribution board is an old Dorman Smith consumer unit which is now obsolete and should be replaced | Replace the board with a new consumer unit. | N/A | [5 empty] | 1000 |  |  |  |  | 1000
Internal | 1 | Amenity Area | G |  | Electrical Services |  | Sub-mains switchgear |  | Sub distribution wiring and containment systems | Unit rate | 1 | 3000 | C | 2 | R | 25 | within 2 years | 3000 | The existing building wiring was tested in August 2018 and appears to have past these tests, it was not clear from our visual inspection as to the age of the wiring and its overall condition. | As a minimum, repairs of the defects identified by the condition report should be carried out, but consideration should be given to rewiring the building. | N/A | [5 empty] | 3000 |  |  |  |  | 3000
Internal | 1 | 1st Floor Flats | G |  | Electrical Services |  | Sub-mains switchgear |  | Sub distribution wiring and containment systems | Unit rate | 1 | 3000 | C | 3 | R | 25 | 3-5 years | 3000 | The flat wiring is old and nearing the end of its life. | Rewire the 1st floor flats to the latest version of BS7671. | N/A | [6 empty] | 3000 |  |  |  | 3000
Internal | 1 | Bedrooms | G |  | Electrical Services |  | Lighting Systems |  | Emergency lighting (Inc. key switch) | Unit rate | 40 | 200 | B | 2 | R | 5 | within 2 years | 8000 | Bedrooms should be provided with an emergency luminaire | Install a recessed anti-panic emergency luminaire with a new key test switch. | N/A | [5 empty] | 8000 |  |  |  |  | 8000
Internal | 1 | Bedrooms | G |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (internal) | Unit rate | 40 | 40 | B | 2 | R | 20 | within 2 years | 1600 | The existing bedroom pendant luminaire should be provided with a dimmable LED lamp and the general lighting supplemented with additional LED recessed down lighters to provide good light levels | Install new LED luminaires to allow for the residents to be able to read and for nursing staff/doctors to be able to carry out medical examinations in the bed rooms. | N/A | [5 empty] | 1600 |  |  |  |  | 1600
External | 1 | Walkways/escape routes | G |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (external) | Unit rate | 1 | 12500 | C | 2 | R | 20 | within 2 years | 12500 | Around the external walkways there are emergency luminaires over the exit doors but there area areas of walkway with no illumination, general and emergency illumination should be installed especially where there is a change in direction or a very narrow walkway. | Install general external luminaires around the building to illuminate the escape routes, luminaires to be controlled by photocells and provided with 3 hour emergency battery back-up. | N/A | [5 empty] | 12500 |  |  |  |  | 12500
Internal | 1 | Bedrooms | G |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (internal) | Unit rate | 40 | 100 | C | 1 | R | 20 | Urgent | 4000 | Provision of table lamps in bedrooms | Place a table lamp in each bedroom | N/A |  |  |  |  | 4000 | [5 empty] | 4000
Internal | 1 | Bedrooms | G |  | Electrical Services |  | Lighting Systems |  | Lighting control and management systems | Unit rate | 1 | 3000 | B | 3 | R | 20 | 3-5 years | 3000 | Light switches should be replaced with new switches with colour contrast colour plates and new dimmer switches for the pendant luminaire should be installed. | Replace the existing light switches with new switches. | N/A | [6 empty] | 3000 |  |  |  | 3000
Internal | 1 | Bedrooms | G |  | Electrical Services |  | Protection Systems |  | Fire Alarm Installations (Inc., call points, sounders and detection) | Unit rate | 1 | 7500 | C | 1 | R | 25 | Urgent | 7500 | The bedroom smoke detector should be replaced with a new addressable detector with a sounder and a beacon/VAD. | Replace the fire alarm system with a new addressable system. | N/A |  |  |  |  | 7500 | [5 empty] | 7500
Internal | 1 | Corridor | G |  | Electrical Services |  | Lighting Systems |  | Emergency lighting (Inc. key switch) | Unit rate | 1 | 10000 | C | 1 | R | 25 | Urgent | 10000 | The corridors should be provided with illuminated emergency exit signs and installed at all turns and exits from internal rooms. | A review of the current exit signage should be carried out and where the signs do not comply with BS5266, new signs should be installed. | N/A |  |  |  |  | 10000 | [5 empty] | 10000
Internal | 1 | Corridor | G |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (internal) | Unit rate | 1 | 12000 | C | 3 | R | 25 | 3-5 years | 12000 | The existing corridor and amenity area luminaires should be replaced with new LED luminaires to improve energy efficiency. | Install new LED luminaires. | N/A | [6 empty] | 12000 |  |  |  | 12000
Internal | 1 | Corridor | G |  | Electrical Services |  | Lighting Systems |  | Lighting control and management systems | Unit rate | 1 | 5000 | B | 3 | R | 25 | 3-5 years | 5000 | The corridor lighting should be provided with a photocell lighting controls to make use of natural daylight. | All corridor lighting controls should be reviewed and where possible automatic lighting controls should be installed in the corridors. | N/A | [6 empty] | 5000 |  |  |  | 5000
Internal | 1 | Corridor | G |  | Electrical Services |  | Sub-mains switchgear |  | Switched socket outlet (SSO) | Unit rate | 1 | 5000 | B | 3 | R | 25 | 3-5 years | 5000 | Existing small power outlet plates should be of a contrast colour to the walls. | All corridor small power accessories should be replaced with new accessories with a contrasting colour finish to the wall. | N/A | [6 empty] | 5000 |  |  |  | 5000
Internal | 1 | 1st Floor Flats | G |  | Electrical Services |  | Sub-mains switchgear |  | Sub distribution wiring and containment systems | Unit rate | 2 | 4000 | B | 3 | R | 25 | 3-5 years | 8000 | Flat wiring and accessories are nearing end of their life and need to be replaced | Rewire the two flats including new distribution boards, accessories and lighting. | N/A | [6 empty] | 8000 |  |  |  | 8000
Internal | 1 | Corridor | G |  | Electrical Services |  | Protection Systems |  | Fire Alarm Installations (Inc., call points, sounders and detection) | Unit rate | 1 | 10000 | C | 1 | R | 25 | Urgent | 10000 | The corridor smoke detector should be replaced with a new addressable detector with a sounder and a beacon/VAD. | Replace the fire alarm system with a new addressable system. | N/A |  |  |  |  | 10000 | [5 empty] | 10000
Internal | 1 | Boiler house | G |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Dosing Pots | Unit rate | 5 | 200 | D | 1 | R | 15 | Urgent | 1000 | No dosing pots installed on heating systems. | Dosing pots to be installed on each heating system | N/A |  |  |  |  | 1000 | [5 empty] | 1000
Internal | 1 | Boiler house | G |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Magnetic Filters | Unit rate | 5 | 200 | D | 1 | R | 10 | Urgent | 1000 | New boilers have been installed on existing old heating systems. Magnetic filters have been fitted in two of the boiler houses, the remainder should be installed to protect boilers/pumps | Magnetic filters to be installed on each heating system | N/A |  |  |  |  | 500 | [5 empty] | 500
Internal | 1 | Boiler house | G |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Pressure relief discharges/Tundish | Unit rate | 15 | 125 | D | 1 | H | 20 | Urgent | 1875 | Many of the various pressure relief discharges do not discharge into tundishes but directly onto the floor. This is a health and safety hazard. | All discharges to terminate within a tundish and connected directly to a drain. | N/A |  |  |  |  | 1875 | [5 empty] | 1875
Internal | 1 | Boiler house | G |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Expansion Vessels | Unit rate | 5 | 250 | D | 1 | R | 15 | Urgent | 1250 | Expansion vessels do not appear to have correct number of valves and drain off points. To be reviewed. | Expansion vessels need to be reviewed and valves drain off points installed if required. | N/A |  |  |  |  | 1250 | [5 empty] | 1250
Internal | 1 | Boiler house | G |  | Mechanical Services |  | Heating Distribution |  | Heating Services Thermal Insulation | Unit rate | 5 | 1750 | D | 1 | Q | 30 | Urgent | 1750 | Heating pipework within boiler houses have insulation to the majority of pipework, but there are a number of sections of missing insulation. All valves to be provided with insulated jackets | Install thermal insulation to all missing sections of pipework within boiler houses and install insulation jackets to all valves. | N/A |  |  |  |  | 1750 | [5 empty] | 1750
Internal | 1 | Throughout | G |  | Mechanical Services |  | Heating Distribution |  | Heating Distribution Pipework | Unit rate | 1 | 30000 | C | 3 | R | 25 | 3-5 years | 30000 | Existing distribution is coming to end of life and is a one pipe heating circuit throughout. | Consideration should be given to replacing existing heating distribution system with a new 2 pipe VT heating distribution system. All pipework should be insulated throughout their length. | N/A | [6 empty] | 30000 |  |  |  | 30000
Internal | 1 | Throughout | G |  | Mechanical Services |  | Heating Distribution |  | Radiators | Unit rate | 100 | 500 | C | 3 | R | 20 | 3-5 years | 25000 | Some of the existing radiators are nearing their end of life and looking tired and outdated. | Consideration should be given to replacing the existing radiators with new LST radiators and thermostatic mixing valves to ensure that the heating system can operate correctly and be controllable. | N/A | [6 empty] | 25000 |  |  |  | 25000
Internal | 1 | Boiler house | G |  | Mechanical Services |  | Heating Controls |  | BMS | Unit rate | 1 | 10000 | C | 3 | R | 20 | 3-5 years | 10000 | Existing controls are old and very basic | The existing basic controls should be considered to be replaced with a more energy efficient BMS system to control all heating and hot water systems. | N/A | [6 empty] | 10000 |  |  |  | 10000
Internal | 1 | Boiler house | G |  | Mechanical Services |  | Hot Water Plant & Equipment |  | Calorifiers | Unit rate | 5 | 2000 | B | 3 | R | 20 | 3-5 years | 10000 | The calorifiers are coming to the end of their life and are no longer manufactured. | We would recommend to look at replacing the existing calorifiers with new more energy efficient models. | N/A | [6 empty] | 10000 |  |  |  | 10000
Internal | 1 | Throughout | G |  | Mechanical Services |  | Hot & Cold Water Distribution Services |  | Hot and Cold Water Pipework | Unit rate | 1 | 25000 | C | 3 | R | 25 | 3-5 years | 25000 | Existing distribution is coming to end of life. | Replace existing hot and cold water distribution system with a new. | N/A | [6 empty] | 25000 |  |  |  | 25000
Internal | 1 | W.C.'s | G |  | Mechanical Services |  | Hot & Cold Water Distribution Services |  | Toilets | Unit rate | 3 | 400 | B | 2 | R | 25 | within 2 years | 1200 | Existing black toilet cisterns may contain asbestos, also the overflow discharges onto the floor. | Replace black toilet cistern and toilets with new close coupled toilets with built in overflows. | N/A | [5 empty] | 1200 |  |  |  |  | 1200
Internal | 1 | W.C.'s | G |  | Electrical Services |  | Communication Services |  | Toilets | Unit rate | 8 | 300 | C | 3 | R | 25 | 3-5 years | 2400 | Wi-Fi access to the internet for all bedrooms | Install 2 No IT/Data cables from the data rack to each of the bedroom corridors and install a Wi-Fi module in each corridor. | N/A | [6 empty] | 2400 |  |  |  | 2400
Internal | 1 | Laundry | G |  | Mechanical Services |  | Mechanical Ventilation |  | Galvanised Ductwork Systems | Unit rate | 1 | 900 | B | 1 | R | 25 | Urgent | 900 | There is a possibility of lint build-up in the laundry dryers extract ductwork. It was not clear if it is possible to clean ducts. | Arrange where necessary for the installation of access panels in the duct and clean the ducts to remove any build-up of lint. | N/A |  |  |  |  | 900 | [5 empty] | 900
Internal | 1 | Main Entrance | G |  | Mechanical Services |  | Heating Distribution |  | Fan Convectors | Unit rate | 1 | 2500 | C | 2 | R | 25 | within 2 years | 2500 | Reception fan convector is in poor condition | Replace the existing fan convector with a new unit. | N/A | [5 empty] | 2500 |  |  |  |  | 2500
Internal | 1 | Boiler House | G |  | Electrical Services |  | Sub-mains switchgear |  | Sub distribution wiring and containment systems | Unit rate | 1 | 2500 | C | 2 | R | 25 | within 2 years | 350 | Controls cabling within Blue wing boiler house very untidy and trunking lid missing. | The controls wiring in the blue wing boiler house needs tiding up and the trunking lid installed | N/A | [5 empty] | 350 |  |  |  |  | 350
Internal | 1 | Boiler house | G |  | Electrical Services |  | Protection Systems |  | Fire Alarm Installations (Inc., call points, sounders and detection) | Unit rate | 1 | 75 | C | 2 | R | 25 | within 2 years | 75 | Fire alarm detector hanging down supported by cables. | Re-fix the smoke detector to the soffit. | N/A | [5 empty] | 75 |  |  |  |  | 75
Internal | 1 | Sluice Rooms | G |  | Mechanical Services |  | Mechanical Ventilation |  | Local extract fans | Unit rate | 4 | 750 | C | 2 | R | 25 | within 2 years | 3000 | No extract fans in the sluice rooms. | Install a trickle vent fan in the sluice rooms with a PIR to bring the fan up to full speed when a person enters the room. | N/A | [5 empty] | 3000 |  |  |  |  | 3000
External | 1 | Courtyard by delivery entrance |  |  | Mechanical Services |  | Mechanical Ventilation |  | Local extract fans | Unit rate | 1 | 500 | B | 3 | R | 25 | 3-5 years | 500 | Cooking smells entering the building and courtyard by delivery entrance. | Review and modify the existing ductwork to reduce the smells entering the rooms when doors and windows are open. | N/A | [6 empty] | 500 |  |  |  | 500
[20 empty] | Priority Totals | [5 empty] | 40905 | 171586 | 288682.23 | 257898.23 | 257464.23 | 284594.46
[30 empty] | Overall Total |  | 1301130.15
Internal
364168

## Lookup - Fabric Int
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
CODE | Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | STANDARD RATE | RATE TYPE/ Item, M2, Nr | Cost Notes
10101 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10101 | Suspended Ceiling Tile - Metal | 25 | 134 | m2
10102 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10102 | Mineral fibre suspended ceiling tiles 600 x 600 | 25 | 76.47 | m2 | 1 Man houre and materials from BCIS | Labour set at £23.82/hrs
10103 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10103 | Plasterboard & Skim finish | 35 | 31.9 | m2 | 1 Man houre and materials from BCIS
10104
10105 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10105 | Mineral fibre suspended ceiling tiles 600 x 1200 | 25 | 152.94 | m2 | 1 Man houre and materials from BCIS
10106 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10106 | Exposed Concrete | 85 | 80 | m2
10107 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10107 | Plaster | 35 | x | m2
10108DS | 1 | Internal Finishes | 101 | Ceiling Finishes | 10108DS | Exposed underside of stair | 35 | x | m2
10109 |  | Internal Finishes | 101 | Ceiling Finishes | 10109 | Other 1
10201 | 1 | Internal Finishes | 102 | Wall Finishes | 10201 | Metal / timber stud with plasterboard | 35 | 80 | m2
10202 | 1 | Internal Finishes | 102 | Wall Finishes | 10202 | Blockwork | 85 | 280 | m2
10203 | 1 | Internal Finishes | 102 | Wall Finishes | 10203 | Brickwork | 85 | 265 | m2
10204 | 1 | Internal Finishes | 102 | Wall Finishes | 10204 | Glazed partitions | 30 | TBC | m2
10205 | 1 | Internal Finishes | 102 | Wall Finishes | 10205 | Ceramic Wall Tiles | 35 | 110 | m2 | Hack off and replace with new tiles 200 x 200 including pointing and labour.
10206 | 1 | Internal Finishes | 102 | Wall Finishes | 10206 | Exposed Concrete | 85 | 80 | m2
10207 | 1 | Internal Finishes | 102 | Wall Finishes | 10207 | Plaster on Brick/Block | 35 | 35.38 | m2
10208DS | 1 | Internal Finishes | 102 | Wall Finishes | 10208DS | Pre-finished panels | 25 | x | m2
10301 | 1 | Internal Finishes | 103 | Floor Finishes | 10301 | Sheet Vinyl | 10 | 32.01 | m2 | Labour and mat's from BCIS
10302 | 1 | Internal Finishes | 103 | Floor Finishes | 10302 | Carpet Tile | 15 | 43.58 | m2 | Labour and mat's from BCIS
10303 | 1 | Internal Finishes | 103 | Floor Finishes | 10303 | Carpet Sheet | 15 | 35.02 | m2 | Labour and mat's from BCIS
10304 | 1 | Internal Finishes | 103 | Floor Finishes | 10304 | Concrete | 85 | 80 | m2 | Labour and mat's from BCIS
10305 | 1 | Internal Finishes | 103 | Floor Finishes | 10305 | Quarry Tiles | 15 | 34.3 | m2 | Labour and mat's from BCIS
10306 | 1 | Internal Finishes | 103 | Floor Finishes | 10306 | Sheet Vinyl (slip resistant) | 15 | 42.05 | m2 | Labour and mat's from BCIS
10307 | 1 | Internal Finishes | 103 | Floor Finishes | 10307 | Metal Check Deck | 20 | 24 | m2
10308DS |  | Internal Finishes | 103 | Floor Finishes | 10308DS | Barrier Matting | 20 | 71.71 | m2
10309DS | 1 | Internal Finishes | 103 | Floor Finishes | 10309DS | Vinyl tiles | 15 | 42.05 | m2
10310DS | 1 | Internal Finishes | 103 | Floor Finishes | 10310DS | Raised access tiles | 20 | x | m2
10311 | 1 | Internal Finishes | 103 | Floor Finishes | 10311 | Other | x | x | x
10401 | 1 | Internal Finishes | 104 | Decorations | 10401 | Emulsion paint finish to walls | 5 | 5.31 | m2 | Prepare, 1st coat to previously painted walls. BCIS
10402 | 1 | Internal Finishes | 104 | Decorations | 10402 | Heavy Duty Emulsion Paint Finish | 5 | 7.12 | m2 | Prepare, 1st coat + additional coat to previously painted walls. BCIS
10403 | 1 | Internal Finishes | 104 | Decorations | 10403 | Eggshell paint finish to walls | 5 | 7.12 | m2 | Prepare, 1st coat + additional coat to previously painted walls. BCIS
10404 | 1 | Internal Finishes | 104 | Decorations | 10404 | Decoration to Steel Beams | 7 | 5.13 | m2
10405 | 1 | Internal Finishes | 104 | Decorations | 10405 | Floor Paint | 15 | 25 | m2 | Labour and mat's from BCIS
10406 | 1 | Internal Finishes | 104 | Decorations | 10406 | Emulsion paint finish to Ceiling | 5 | 8.62 | m2 | Labour and mat's from BCIS
10407 | 1 | Internal Finishes | 104 | Decorations | 10407 | Door decorations (internal) | 5 | 6.54 | m2
10408 | 1 | Internal Finishes | 104 | Decorations | 10408 | Decoration of inside window frame | 5 | 5.31 | m2
10409 | 1 | Internal Finishes | 104 | Decorations | 10409 | Joinery decorations (architraves, skirting) | 5 | 7 | m2
10410DS | 1 | Internal Finishes | 104 | Decorations | 10410DS | Decoration of timber surfaces | 5 | 7 | m2
10411 | 1 | Internal Finishes | 104 | Decorations | 10411 | Other 1 | x | x | x
10412 | 1 | Internal Finishes | 104 | Decorations | 10412 | Other 2 | x | x | x
20101 | 2 | Door | 201 | Door | 20101 | Hollow core door (Single) | 20 | 120.73 | Nr
20102 | 2 | Door | 201 | Door | 20102 | Solid veneer faced timber door (Single) | 25 | 157.52 | Nr | Spons page 440
20103 | 2 | Door | 201 | Door | 20103 | Solid veneer faced timber door (Single) with vision panel | 25 | 334 | Nr | Spons page 439
20104 | 2 | Door | 201 | Door | 20104 | Solid veneer faced timber door (Single+Half) | 25 | 445.64 | Nr | Spons page 439
20105 | 2 | Door | 201 | Door | 20105 | Solid veneer faced timber door (Single+Half) with vision panel | 25 | 465.64 | Nr | Spons page 439
20106 | 2 | Door | 201 | Door | 20106 | Solid veneer faced timber door (Double) | 25 | 241.46 | Nr | Spons page 439
20107 | 2 | Door | 201 | Door | 20107 | Solid veneer faced timber door (Double) with vision panel | 25 | 668 | Nr | Spons page 439
20108 | 2 | Door | 201 | Door | 20108 | Glazed Single Leaf | 30 | 140 | Nr
20109 | 2 | Door | 201 | Door | 20109 | Glazed Double Leaf | 30 | 280 | Nr
20110 | 2 | Door | 201 | Door | 20110 | Metal Roller Shutter | 20 | 1309 | Nr | Spons page 444 (3000mm x 1000mmm)
20111 | 2 | Door | 201 | Door | 20111 | Aluminium door with factory applied powder coat finish | 35 | 486 | Nr
20112 | 2 | Door | 201 | Door | 20112 | Steel security door / cell door | 40 | x | x
20113DS | 2 | Door | 201 | Door | 20113DS | Fire door furniture | 25 | x | Item
20114 | 2 | Door | 201 | Door | 20114 | Other 1 | x | x | x
30101 | 3 | Ironmongery | 301 | Ironmongery | 30101 | Ironmongery (general item) | 20 | x | Item
40101 | 4 | Joinery | 401 | Joinery | 40101 | Timber / MDF architraves | 25 | 8.6 | lm
40102 | 4 | Joinery |  | Joinery | 40102 | Timber skirting | 25 | 7 | lm
40103DS | 4 | Joinery |  | Joinery | 40103DS | Timber dado / picture rail | 25 | 7 | lm
40104DS | 4 | Joinery |  | Joinery | 40104DS | Timber sub frame / sill / general surfaces | 25 | 7 | lm
40105DS | 4 | Joinery |  | Joinery | 40105DS | Ply boxing | 25 | 38.4 | m
40105 | 4 | Joinery |  | Joinery | 40105 | Other | x | x | x
50101 | 5 | Sanitary ware | 501 | WC | 50101 | Vitreous China | 20 | 307.91 | Item | Remove and replace with new + labour BCIS
50102 | 5 | Sanitary ware | 501 | WC | 50102 | Stainless Steel | 20 | 473.5 | Item
50201 | 5 | Sanitary ware | 502 | Sink | 50201 | Vitreous China | 20 | 289.34 | Item | Remove and replace with new + labour BCIS
50202 | 5 | Sanitary ware | 502 | Sink | 50202 | Stainless Steel | 20 | 473.5 | Item | Remove and replace with new + labour BCIS
50203 | 5 | Sanitary ware | 502 | Sink | 50203 | Cleaners sink (Belfast etc) | 20 | 307.91 | Nr | Remove and replace with new + labour BCIS
50301 | 5 | Sanitary ware | 503 | Urinal | 50301 | Vitreous China | 15 | 609.85 | Item | Remove and replace with new + labour BCIS
50302 | 5 | Sanitary ware | 503 | Urinal | 50302 | Stainless Steel | 20 | 609.85 | Item | Remove and replace with new + labour BCIS
50401 | 5 | Sanitary ware | 504 | Vanity Unit | 50401 | High Pressure Laminated Chipboard | 20 | 650 | Item |  | http://www.washroomcubicles.co.uk/healthcare-ips-panel-system/
50501 | 5 | Sanitary ware | 505 | Cubicles | 50501 | High Pressure Laminated Chipboard | 20 | 650 | Item
50601 | 5 | Sanitary ware | 506 | IPS | 50601 | High Pressure Laminated Chipboard | 20 | 650 | Item
50701 | 5 | Sanitary ware | 507 | Other | 50701 | Other | x | x | x
60101 | 6 | Windows | 601 | Internal glazing | 60101 | Metal frame | 35 | TBC | Nr
60102 | 6 | Windows | 601 | Internal glazing | 60102 | Softwood Timber | 25 | 50.28 | Nr | Remove and replace with new + labour BCIS
60103 | 6 | Windows | 601 | Internal glazing | 60103 | PVCu Double Glazed Unit | 35 | 350 | Nr
60104 | 6 | Windows | 601 | Internal glazing | 60104 | Other | x | x | x
70101 | 7 | FF&E | 701 | FF&E | 70101 | Grab Rails - Vertical | 20 | 27.41 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70102 | 7 | FF&E | 701 | FF&E | 70102 | Grab Rails - Drop down | 20 | 42.91 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70103 | 7 | FF&E | 701 | FF&E | 70103 | Hand Rails | 20 | 27.41 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70104 | 7 | FF&E | 701 | FF&E | 70104 | Soap dispensers | 10 | 1 | Item
70105 | 7 | FF&E | 701 | FF&E | 70105 | Kitchen Units | 15 | 1 | Item
70106 | 7 | FF&E | 701 | FF&E | 70106 | Paper towel dispensers | x | TBC | Nr
70107 | 7 | FF&E | 701 | FF&E | 70107 | Toilet paper dispensers | x | TBC | Nr
70108 | 7 | FF&E | 701 | FF&E | 70108 | Metal Access Stairs | 25 | Varies | Item
70109DS | 7 | FF&E | 701 | FF&E | 70109DS | Laminate worktop on metal legs | 15 |  | Item
70110DS | 7 | FF&E | 701 | FF&E | 70110DS | Blinds | 15 | x | Item
70111DS | 7 | FF&E | 701 | FF&E | 70111DS | Worktop & units | 15 | x | Item
70112DS | 7 | FF&E | 701 | FF&E | 70112DS | Benches | 20 | x | Item
70113DS | 7 | FF&E | 701 | FF&E | 70113DS | Built in cupboards etc | 20 | x | Item
70114DS | 7 | FF&E | 701 | FF&E | 70114DS | Roller racking | 20 |  | Item
70115DS | 7 | FF&E | 701 | FF&E | 70115DS | Metal handrail | 20 |  | Item
70116DS | 7 | FF&E | 701 | FF&E | 70116DS | Timber staircase | 35 |  | Item
70117 | 7 | FF&E | 701 | FF&E | 70117 | Other | x | x | x

## Lookup - Fabric Ext
CODE | Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | STANDARD RATE | RATE TYPE/ Item, M2, Nr | Cost Notes
10101 | 1 | External Landscaping | 101 | Hard Landscaping | 10101 | Tarmacadam | 20 |  | m2
10102 |  |  |  |  | 10102 | Concrete | 30 |  | m2
10103 |  |  |  |  | 10103 | Block Paving | 30 |  | m2
10104 |  |  |  |  | 10104 | Paving Slabs | 30 |  | m2
10201 |  |  | 102 | Soft Landscaping | 10201 | Shrubs & Bushes | 20 |  | Item
10202 |  |  |  |  | 10202 | Grass | 20 |  | m2
20101 | 2 | Roads and Car Parks | 201 | Roads | 20101 | Tarmacadam | 20 |  | m2
20201 |  |  | 202 | Car Parks | 20201 | Tarmacadam | 20 |  | m2
30101 | 3 | Street Furniture | 301 | Bollards | 30101 | Concrete | 30 |  | Item
30102 |  |  |  |  | 30102 | Brushed Aluminium | 25 |  | Item
30103 |  |  |  |  | 30103 | Mild Steel | 20 |  | Item
30201 |  |  | 302 | Benches | 30201 | Timber | 20 |  | Item
30202 |  |  |  |  | 30202 | GRP | 35 |  | Item
30203 |  |  |  |  | 30203 | Metal | 25 |  | Item
40101 | 4 | Building Superstructure | 401 | Roofs - Pitched | 40101 | Slate tile | 75 |  | m2
40102 |  |  |  |  | 40102 | Concrete Tiles | 40 |  | m2
40103 |  |  |  |  | 40103 | Clay tiles | 65 |  | m2
40104 |  |  |  |  | 40104 | Other |  |  | m2
40201 |  |  | 402 | Roofs - Flat | 40201 | Single Ply Membrane | 25 |  | m2
40202 |  |  |  |  | 40202 | Built up Felt System | 20 |  | m2
40203 |  |  |  |  | 40203 | Other
40301 |  |  | 403 | Roof Drainage | 40301 | Pressed Metal Gutters & Downpipes | 20 |  | lm
40302 |  |  |  |  | 40302 | Cast Iron Gutters & Downpipes | 50 |  | lm
40303 |  |  |  |  | 40303 | PVCu Gutters & Downpipes | 25 |  | lm
40304 |  |  |  |  | 40304 | Aluminium Gutters & Downpipes | 30 |  | lm
40305 |  |  |  |  | 40305 | Clearing of gutters | 5 |  | lm
40401 |  |  | 404 | Roof Lights | 40401 | Aluminium Framed Glazing | 30 |  | Nr
40402 |  |  |  |  | 40402 | Proprietary Unit | 25 |  | Nr
40403 |  |  |  |  | 40403 | Velux Window | 25 |  | Nr
40501 |  |  | 405 | Wall Structure | 40501 | Blockwork | 85 |  | m2
40502 |  |  |  |  | 40502 | Brickwork | 85 |  | m2
40503 |  |  |  |  | 40503 | Steel | 85 |  | m2
40504 |  |  |  |  | 40504 | Concrete | 80 |  | m2
40505 |  |  |  |  | 40505 | Modular | 30 |  | m2
40506 |  |  |  |  | 40506 | Other
40601 |  |  | 406 | Wall Finishes | 40601 | Ceramic Tiles | 25 |  | m2
40602 |  |  |  |  | 40602 | Plaster | 50 |  | m2
40603 |  |  |  |  | 40603 | Timber | 25 |  | m2
40604 |  |  |  |  | 40604 | Render Plaster | 25 |  | m2
40605 |  |  |  |  | 40605 | Proprietary Cladding | 40 |  | m2
40606 |  |  |  |  | 40606 | Glazing Curtain Wall | 60 |  | m2
40607 |  |  |  |  | 40607 | Brickwork | 40 |  | m2
40608 |  |  |  |  | 40608 | Blockwork | 30 |  | m2
40609 |  |  |  |  | 40609 | Aluminium Cladding | 40 |  | m2
40701 |  |  | 407 | Decorations | 40701 | External block / brick | 5
40702 |  |  |  |  | 40702 | Timber doors | 5
40703 |  |  |  |  | 40703 | Timber windows | 5
40704 |  |  |  |  | 40704 | Metal doors | 5
40705 |  |  |  |  | 40705 | Metal windows | 5
40706 |  |  |  |  | 40706 | Emulsion to render | 5
40707 |  |  |  |  | 40707 | cast iron RWGs | 5
40708 |  |  |  |  | 40708 | Timber generally (soffits/fascias) | 5
40709 |  |  |  |  | 40709 | Other | 5
40801 |  |  | 408 | Soffits / fascias | 40801 | Timber | 15 |  | m2
40802 |  |  |  |  | 40802 | PVCu | 25 |  | m2
40803 |  |  |  |  | 40803 | Aluminium | 30
40901 |  |  | 409 | Upper Floors | 40901 | Cast In-situ Concrete | 80 |  | m2
40902 |  |  |  |  | 40902 | Block & Beam | 80 |  | m2
40903 |  |  |  |  | 40903 | Steel | 85 |  | m2
40904 |  |  |  |  | 40904 | Suspended timber | 70
41001 |  |  | 410 | Windows (inc grilles/louvres) | 41001 | Powder Coated Aluminium | 45 |  | Nr
41002 |  |  |  |  | 41002 | Metal | 45 |  | Nr
41003 |  |  |  |  | 41003 | Softwood Timber | 35 |  | Nr
41004 |  |  |  |  | 41004 | PVCu Double Glazed Unit | 35 |  | Nr
41005 |  |  |  |  | 41005 | Alum. Louvres | 45
41006 |  |  |  |  | 41006 | Alum. Grilles | 45
41101 |  |  | 411 | Doors | 41101 | Powder Coated Aluminium | 30 |  | Nr
41102 |  |  |  |  | 41102 | PVCu Double Glazed Unit | 30 |  | Nr
41103 |  |  |  |  | 41103 | Glazed Doors | 30 |  | Nr
41104 |  |  |  |  | 41104 | Metal Lourve Door | 30 |  | Nr
41105 |  |  |  |  | 41105 | High Speed Fabric Door | 25 |  | Nr
41201 |  |  | 412 | Frame | 41201 | Concrete | 80 |  | m2
41202 |  |  |  |  | 41202 | Steel | 85 |  | m2
41203 |  |  |  |  | 41203 | L/B brickwork | 85
41301 |  |  | 413 | Roof frame | 41301 | Timber | 70
41302 |  |  |  |  | 41302 | Steel | 85
41401 |  |  | 414 | Stairs | 41401 | Concrete | 85 |  | Nr
41402 |  |  |  |  | 41402 | Steel | 85 |  | Nr
41501 |  |  | 415 | External canopies / structures | 41501 | Canopies fixed to block
41502 |  |  |  |  | 41502 | Freestading canopy
41503 |  |  |  |  | 41503 | Bike Shelter
41504 |  |  |  |  | 41504 | Smoking Shelter
41601 |  |  | 416 | Balustrades & Handrails | 41601 | Timber | 25 |  | lm
41602 |  |  |  |  | 41602 | Metal | 35 |  | lm
50101 | 5 | Fencing | 501 | Fencing & Security | 50101 | Concrete post & wire | 25 |  | m2
50102 |  |  |  |  | 50102 | Timber post & wire | 20 |  | m2
50103 |  |  |  |  | 50103 | Timber boards | 15 |  | m2
50104 |  |  |  |  | 50104 | Concrete posts | 25 |  | lm
50105 |  |  |  |  | 50105 | Chain link | 20 |  | lm
50106 |  |  |  |  | 50106 | Mild steel railings | 12 |  | lm
50107 |  |  |  |  | 50107 | Wrought iron railings | 25 |  | lm
50108 |  |  |  |  | 50108 | Galvanised/painted | 20 |  | lm
50109 |  |  |  |  | 50109 | Galanised security gates | 20 |  | Nr
50110 |  |  |  |  | 50110 | Other | x
60101 | 6 | Sub Structure | 601 | Foundations | 60101 | Concrete | 110 |  | lm
7

## Element look up - M+E
Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | REDUCED LIFE DUE TO USAGE | STANDARD RATE | RATE TYPE/ Item, M2, Nr
1 | Mechanical Services | 101 | Heating Plant & Auxiliaries | 10101 | Gas fired boiler <100kw | 20 | 12 |  | Nr
|  |  |  | 10102 | Gas fired boiler 100kw - 300kw | 25 | 15 |  | Nr
|  |  |  | 10103 | Gas fired boiler 300kw - 500kw | 25 | 20 |  | Nr
|  |  |  | 10104 | Gas fired boiler 500kw + | 25 | 20 |  | Nr
|  |  |  | 10105 | Flue Systems (stainless steel 200 kw boiler) | 30 | 25 |  | Nr
|  |  |  | 10106 | Fan Flues Systems. | 25 | 15 |  | Item
|  |  |  | 10107 | Commerical Circulating Pump (Single or dual type) | 20 | 15 |  | Nr
|  |  |  | 10108 | Centrifugal pumps | 20 | 15 |  | Nr
|  |  |  | 10109 | Heating pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10110 | Combined heating / chilled water pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10111 | Expansion vessel (unvented hot water) | 15 | 10 |  | Nr
|  |  |  | 10112 | Gas fired warm air heaters. | 20 | 20 |  | Nr
|  |  |  | 10113 | Dosing pots | 15 | 15 |  | Nr
|  |  |  | 10114 | Sump and well pumps | 12 | 12 |  | Nr
|  |  |  | 10115 | Air-to-air commercial Heat pumps | 15 | 15 |  | Nr
|  |  |  | 10116 | Water-to-air commerical Heat pumps | 15 | 15 |  | Nr
|  |  |  | 10117 | Water treatment equipment | 15 | 15 |  | Item
|  | 102 | Heating Distribution | 10201 | Heating Distribution Pipework | 25 | 25 |  | m2
|  |  |  | 10202 | Heating Services thermal insulation | 30 | 30 |  | m2
|  |  |  | 10203 | Plant Manual Isolation Valves | 25 | 15 |  | Item
|  |  |  | 10204 | Radiators. | 20 | 20 |  | Nr
|  |  |  | 10205 | Radiant Panels | 20 | 20 |  | Nr
|  |  |  | 10206 | Fan Convectors | 20 | 15 |  | Nr
|  |  |  | 10207 | Natural Convectors | 20 | 20 |  | Nr
|  |  |  | 10208 | Underfloor heating steel pipes & Manifolds | 30 | 15 |  | m2
|  |  |  | 10209 | LTHW Warm air heaters | 15 | 15 |  | Nr
|  |  |  | 10210 | Electric Heaters. | 10 | 10 |  | Nr
|  |  |  | 10211 | Expansion Bellow. | 10 | 10 |  | Nr
[5 empty] | Motorised Actuators | 10
|  |  |  | 10212 | Steam Pipework system | 25 | 20 |  | m2
|  | 103 | Heating Controls | 10301 | Building Management Systems | 15 | 15 |  | Item
|  |  |  | 10302 | Control Panels | 20 | 15 |  | Nr
|  |  |  | 10303 | Motorised Control Valves | 15 | 15 |  | Nr
|  | 104 | Fuel Services | 10401 | Gas distribution pipework | 25 | 25 |  | m2
|  |  |  | 10402 | Oil distribution pipework | 25 | 25 |  | m2
|  |  |  | 10403 | Fuel Booster Pumps | 15 | 15 |  | Nr
|  |  |  | 10404 | Fuel shut-off valves | 25 | 20 |  | Nr
|  |  |  | 10405 | Fuel storage tank. | 20 | 20 |  | Nr
|  |  |  | 10406 | Medical Gases | 20 | 20 |  | m2
|  |  |  | 10407 | Fuel Meter & Measurement | 20 | 20 |  | Item
|  | 105 | Cold Water Plant & Equipment | 10501 | Mains cold water booster | 15 | 15 |  | Nr
|  |  |  | 10502 | Cold Water Storage Tanks | 25 | 20 |  | Nr
|  |  |  | 10503 | Sprinkler | 20 | 20 |  | m2
|  | 106 | Hot & Cold Water Distribution Services | 10601 | Hot and Cold Water Pipework systems | 25 | 25 |  | m2
|  |  |  | 10602 | Hot & Cold Water Services thermal insulation | 30 | 20 |  | m2
|  |  |  | 10603 | Hot water temperature mixing valve | 10 |  |  | Nr
|  |  |  | 10604 | Shower mixer and head | 10 | 10 |  | Nr
|  |  |  | 10605 | Water Meter & Measurement | 20 | 15 |  | Item
|  | 107 | Hot Water Plant & Equipment | 10701 | Calorifiers (Copper/ Mild Steel) | 20 | 15 |  | Nr
|  |  |  | 10702 | Circulating Pumps | 15 | 15 |  | Nr
|  |  |  | 10703 | Electric hot water heaters | 15 | 10 |  | Nr
|  |  |  | 10704 | Gas fired hot water heaters | 20 | 15 |  | Nr
|  |  |  | 10705 | Heat Exchanger (Plate / Shell and tube) | 20 | 10 |  | Nr
|  |  |  | 10706 | Water Boilers - (tea points) | 15 | 10 |  | Nr
|  | 108 | Mechanical Ventilation | 10801 | Packaged Air handling units | 20 | 20 |  | Nr
|  |  |  | 10802 | Roof mounted units fans | 15 | 15 |  | Nr
|  |  |  | 10803 | Axial fans (inline) | 15 | 15 |  | Nr
|  |  |  | 10804 | Centrifugal fans | 20 | 15 |  | Nr
|  |  |  | 10805 | Local extract fans | 10 | 10 |  | Nr
|  |  |  | 10806 | Stair / lobby ventilation | 20 | 20 |  | Item
|  |  |  | 10807 | Galvanised Ductwork Systems | 40 | 40 |  | m2
|  |  |  | 10808 | Ductwork thermal insulation | 30 | 30 |  | m2
|  |  |  | 10809 | External louvres steel painted | 20 | 20 |  | Nr
|  |  |  | 10810 | Fire Dampers | 10 | 10 |  | Nr
|  |  |  | 10811 | Grilles and diffusers | 25 | 25 |  | Nr
|  |  |  | 10812 | Humidifier | 15 | 15 |  | Nr
|  |  |  | 10813 | VAV terminal units | 15 | 15 |  | Nr
|  |  |  | 10814 | Kitchen Extract canopies/ Hoods (average) | 30 | 20 |  | Item
|  |  |  | 10815 | Ductwork Heating/ cooiling coils | 25 | 20 |  | Item
|  | 109 | Chilled Water Plant & Equipment | 10901 | Absorption / Centrifugal Chiller 100kw - 300kw | 25 | 20 |  | Nr
|  |  |  | 10902 | Absorption / Centrifugal Chiller 300kw - 500kw | 25 | 20 |  | Nr
|  |  |  | 10903 | Absorption / Centrifugal Chiller 500kw + | 25 | 20 |  | Nr
|  |  |  | 10904 | Circulating Commerical Pump (single or dual type) | 20 | 15 |  | Nr
|  |  |  | 10905 | Refrigerant leak detector | 10 | 10 |  | Item
|  |  |  | 10906 | Trace heating | 20 | 15 |  | m2
|  |  |  | 10907 | Air cooled/ Evaporative condensers | 20 | 15 |  | Nr
|  |  |  | 10908 | Chilled Water storage vessel | 20 | 20 |  | Nr
|  |  |  | 10909 | Chilled Water pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10910 | Chilled Water Pipework & Valve | 25 | 25 |  | m2
|  |  |  | 10911 | Chilled Water Services thermal insulation | 30 | 20 |  | m2
|  | 110 | Comfort Cooling | 11001 | Fan coil units (heating and cooling) | 15 | 15 |  | Nr
|  |  |  | 11002 | Split systems | 10 | 10 |  | Nr
|  |  |  | 11003 | Computer room air conditioning | 15 | 15 |  | Item
|  |  |  | 11004 | Air conditioning terminal units chilled beams | 20 | 20 |  | Nr
|  |  |  | 11005 | Refrigerant pipework systems | 30 | 30 |  | m2
|  |  |  | 11006 | Condensate pipework system | 15 | 15 |  | m2
|  |  |  | 11007 | VRV units | 15 | 15 |  | Nr
|  | 111 | Miscellaneous Mechanical Equipment & Plant | 11101 | Air compressor | 20 | 20 |  | Nr
|  |  |  | 11102 | Compressed air reciever | 20 | 20 |  | Nr
|  |  |  | 11103 | Pneumatic controls lampsom | 20 | 15 |  | Item
|  |  |  | 11104 | Other |  |  |  | Nr
2 | Electrical Services | 201 | Mains Power Supplies | 20101 | HV switchgear (external) | 30 | 30 |  | Item
|  |  |  | 20102 | Transformers (dry type) | 30 | 30 |  | Nr
|  |  |  | 20103 | LV switchgear (internal) | 25 | 25 |  | Item
|  |  |  | 20104 | Main supply switchgear | 30 | 30 |  | Item
|  |  |  | 20105 | SWA mains/sub distribution cables. | 35 | 35 |  | m2
|  |  |  | 20106 | Earth bonding (Primary) | 30 | 30 |  | Item
|  |  |  | 20107 | Electricity Meter & Measurement | 20 | 20 |  | Item
|  | 202 | Sub-Main Distribution | 20201 | Consumer units | 20 | 20 |  | Nr
|  |  |  | 20202 | Distribution boards (critical) | 20 | 20 |  | Nr
|  |  |  | 20203 | Distribution boards (Non critical) | 20 | 20 |  | Nr
|  |  |  | 20204 | Feeder pillar | 20 | 20 |  | Nr
|  |  |  | 20205 | Inverters | 10 | 10 |  | Nr
|  |  |  | 20206 | Sub distribution wiring and containment systems | 25 | 25 |  | m2
|  |  |  | 20207 | Fixed appliance power supplies/ isolators (Spurs) | 25 | 25 |  | Nr
|  |  |  | 20208 | Switched socket outlet (SSO) | 20 | 20 |  | Nr
|  | 203 | Lighting Systems | 20301 | Emergency lighting (inc key switch) | 25 | 20 |  | Nr
|  |  |  | 20302 | Lighting and luminaires (external) | 15 | 15 |  | Nr
|  |  |  | 20303 | Lighting and luminaires (internal) | 20 | 20 |  | Nr
|  |  |  | 20304 | Lighting control and management systems | 15 | 15 |  | Item
|  | 204 | Protection Systems | 20401 | Access control | 15 | 15 |  | Item
|  |  |  | 20402 | Closed Circuit Television (CCTV) | 20 | 15 |  | m2
|  |  |  | 20403 | Nurse Call Alarm | 15 | 15 |  | m2
|  |  |  | 20404 | Distress Call Alarm | 15 | 15 |  | Item
|  |  |  | 20405 | Fire Alarm Installations (inc, call points, sounders and detection) | 20 | 20 |  | m2
|  |  |  | 20406 | Computer room fire extinguishing system | 15 | 15 |  | m2
|  |  |  | 20407 | Wet/ Dry Riser | 25 | 25 |  | Item
|  |  |  | 20408 | Smoke ventilation systems | 30 | 30 |  | Item
|  |  |  | 20409 | Intruder alarms and intercommunications | 15 | 15 |  | m2
|  |  |  | 20410 | Lightning protection | 25 | 25 |  | m2
|  |  |  | 20411 | Leak Detection | 10 | 10 |  | m2
|  | 205 | Communication System | 20501 | Communication systems | 20 | 20 |  | m2
|  |  |  | 20502 | Public address systems | 20 | 15 |  | m2
|  |  |  | 20503 | Television and satelite systems | 15 | 15 |  | m2
|  | 206 | Lifting Equipment | 20601 | Lift Plant & Controls | 30 | 25 |  | Item
|  |  |  | 20602 | Lift Car refurbishment | 15 | 15 |  | Item
|  |  |  | 20603 | Stair Lifts | 20 | 15 |  | Item
|  |  |  | 20604 | Lifting Hoists | 20 | 15 |  | Item
|  | 207 | Power Generation | 20701 | Combined heat and power (CHP) (gas fired) | 20 | 15 |  | Nr
|  |  |  | 20702 | Standby genernator plus prime mover | 30 | 30 |  | Item
|  |  |  | 20703 | Uninterruptible power supply (UPS) systems | 20 | 20 |  | Item
|  | 208 | Miscellaneous Electrical Equipment & Plant | 20801 | Hand dryer | 5 | 5 |  | Nr
|  |  |  | 20802 | Incinerators | 15 | 15 |  | Item
|  |  |  | 20803 | Kitchen (cooking and support systems) | 15 | 15 |  | Item
|  |  |  | 20804 | Laundries (equipment and support systems) | 20 | 20 |  | Item
|  |  |  | 20805 | Photocoltaic panels | 25 | 25 |  | Nr
|  |  |  | 20806 | Open door with obstacle detector | 20 | 20 |  | Item
|  |  |  | 20807 | Mechanical Roller Shutter Doors | 15 | 15 |  | Item
|  |  |  | 20808 | Theatre clocks | 15 | 15 |  | Item
|  |  |  | 20809 | Other |  |  |  | Nr

## Master Sheet Summary
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Briar Close HOP - 25 Year Master Cost Plan
1 | Preliminaries | 1 | Item | 0 | 0
2 | Ceilings | 1 | Item | 0 | 0
3 | External walls, windows & Doors | 1 | Item | 147258 | 147258
4 | Floors and Stairs | 1 | Item | 141942 | 141942
5 | Internal Walls & Doors | 1 | Item | 54910 | 54910
6 | Redecorations | 1 | Item | 257235.15 | 257235.15
7 | Roofs | 1 | Item | 354625 | 354625
8 | Sanitary Services | 1 | Item | 98950 | 98950
9 | Fixed Furniture and Fittings | 1 | Item | 4250 | 4250
9 | External Areas | 1 | Item | 30060 | 30060
10 | Mechanical Services | 1 | Item | 114475 | 114475
11 | Electrical Services | 1 | Item | 97425 | 97425
12 | Sub-total |  |  |  | 1301130.15
.
13 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 195169.5225
.
14 | Preliminaries Site Specific Costs (scaffold etc,,,) |  |  |  | 30000
15 | Sub-total |  |  |  | 1526299.6725
16 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 0
17 | Provisional Uplift for Sectional Works @ 25% |  |  |  | 389074.9181
18 | Sub-total |  |  |  | 1915374.5906
19 | Contractor Management Fee @ 3.25% |  |  |  | 0
20 | Sub-total |  |  |  | 1915374.5906
21 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 287306.1886
22 | Sub-total |  |  |  | 2202680.7792
23 | Risk Allowance @ 10% |  |  |  | 220268.0779
24 | Client Contingency @10% |  |  |  | 220268.0779
25 | Sub-total |  |  |  | 2643216.9351
26 | Professional fees, surveys and stat fees (15%) |  |  |  | 396482.5403
27 | Total Construction Cost (over 25 years) |  |  |  | 3039699.4753
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.
Note: Provisional uplift of 25% for sectional works included. Actual uplift would need to be established on a site by site basis based on the site layout, extent of works required and the practicalities of undertaking that works with minimal disrupion.

## Roofing
DERBYSHIRE COUNTY COUNCIL
Estimate Roof Cost Plan -Briar Close HOP
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Briar Close HOP
Roofing Project Works
1 | Preliminaries | 1 | Item |  | 0
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 0 | 0
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1300 | m2 | 5 | 6500
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 1500 | 1500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 2500 | 2500
3 | Roofs | 1 | Item | 354625 | 354625
3.01 | Recovering the existing pitched roofs and felt flat roof, including all insulation, flashings and rainwater goods. |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
11 | Sub-total |  |  |  | 354625
.
12 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 53193.75
.
13 | Preliminaries Site Specific Costs |  |  |  | 0
14 | Sub-total |  |  |  | 407818.75
15 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 13254.1094
16 | Sub-total |  |  |  | 421072.8594
17 | Contractor Management Fee @ 3.25% |  |  |  | 13684.8679
18 | Sub-total |  |  |  | 434757.7273
19 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 65213.6591
20 | Sub-total |  |  |  | 499971.3864
21 | Risk Allowance @ 10% |  |  |  | 49997.1386
22 | Client Contingency @10% |  |  |  | 49997.1386
23 | Sub-total |  |  |  | 599965.6637
24 | Scape Fee @ 0.95% |  |  |  | 5699.6738
25 | Total Construction Cost |  |  |  | 605665.3375
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.

## Room refurbishment
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Briar Close HOP
Room Refurbishment Project Works
1 | Preliminaries | 1 | Item |  | 0
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 5302.5 | 5302.5
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1300 | m2 | 5 | 6500
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 500 | 500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 1000 | 1000
2 | Internal Walls, Ceilings and Doors | 1 | Item | 54910 | 54910
2.01 | Include for all internal finishes that are life expired, non-compliant or do not meet the suitability requirements |  | Note
2.02 | See full condition survey data and summary report for further cost break down. |  | Note
3 | Floors and Stairs | 1 | Item | 141942 | 141942
3.01 | Sumarise required works |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
4 | Fixed furniture and fittings | 1 | Item | 4250 | 4250
4.01 | Sumarise required works |  | Note
4.02 | See full condition survey data and summary report for further cost break down. |  | Note
5 | Decorations | 1 | Item | 257235.15 | 257235.15
5.01 | Sumarise required works |  | Note
5.02 | See full condition survey data and summary report for further cost break down. |  | Note
6 | Sub-total |  |  |  | 201102
.
7 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 30165.3
.
8 | Preliminaries Site Specific Costs |  |  |  | 0
9 | Sub-total |  |  |  | 231267.3
10 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 7516.1872
11 | Sub-total |  |  |  | 238783.4872
12 | Contractor Management Fee @ 3.25% |  |  |  | 7760.4633
13 | Sub-total |  |  |  | 246543.9506
14 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 36981.5926
15 | Sub-total |  |  |  | 283525.5432
16 | Risk Allowance @ 10% |  |  |  | 28352.5543
17 | Client Contingency @10% |  |  |  | 28352.5543
18 | Sub-total |  |  |  | 340230.6518
19 | Scape Fee @ 0.95% |  |  |  | 3232.1912
20 | Total Construction Cost |  |  |  | 343462.843
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.

## M&E critical works
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Briar Close HOP
Mechanical and Electrial works package
1 | Preliminaries | 1 | Item |  | 11000
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 0 | 0
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1300 | m2 | 5 | 6500
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 500 | 500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 1000 | 1000
2 | Mechanical Services | 1 | Item | 114475 | 114475
2.01 | Replacement of fan coiled units to A Block, undertake detailed review of heating controls to A Block and cleaning of mechanical extract in toilet areas in A Block and B Block. |  | Note
2.02 | See full condition survey data and summary report for further cost break down. |  | Note
3 | Electrical Services | 1 | Item | 97425 | 97425
3.01 | Replace existing light fitting with new LED and replace life expired fire alarm systems to A and B Block. |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
4 | Builders work in connection | 1 | Item | 0 | 0
4.01 | Take down ceilings, reinsate compartmentation etc… |  | Note
4.02 | See full condition survey data and summary report for further cost break down. |  | Note
5 | Sub-total |  |  |  | 211900
.
6 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 31785
.
7 | Preliminaries Site Specific Costs |  |  |  | 11000
8 | Sub-total |  |  |  | 254685
9 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 8277.2625
10 | Sub-total |  |  |  | 262962.2625
11 | Contractor Management Fee @ 3.25% |  |  |  | 8546.2735
12 | Sub-total |  |  |  | 271508.536
13 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 40726.2804
14 | Sub-total |  |  |  | 312234.8164
15 | Risk Allowance @ 10% |  |  |  | 31223.4816
16 | Client Contingency @10% |  |  |  | 31223.4816
17 | Sub-total |  |  |  | 374681.7797
18 | Scape Fee @ 0.95% |  |  |  | 3559.4769
19 | Total Construction Cost |  |  |  | 378241.2566
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.