## Summary Table
Turn off all excluding C & D grades
Row Labels | Count of CONDITION RANK | Average of Estimated Remaining Useful Design Life (YEARS) | Sum of Year 1 - 2018/19 | Sum of Year 2 - 2019/20 | Sum of Year 3 - 2020/21 | Sum of Year 4 - 2021/22 | Sum of Year 5 - 2022/23 | Sum of Total | Row Labels | Average of Likelihood Score (1-4) | Average of Consequence Score (1-5)
Protection Systems | [8 empty] | Ceiling Finishes
Fire Alarm Installations (inc, call points, sounders and detection) | [8 empty] | Mineral fibre suspended ceiling tiles 600 x 600
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Fire Alarm Installations (inc, call points, sounders and detection) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Protection Systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Mineral fibre suspended ceiling tiles 600 x 600 Total | 2.6571 | 2
Ceiling Finishes | [8 empty] | Suspended Ceiling Tile - Metal
Mineral fibre suspended ceiling tiles 600 x 600 | [8 empty] | MODERATE | 3 | 2
B | 43 | 9.7674 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 35 | 2.6286 | 0 | 19956.3759 | 15934.8186 | 0 | 0 | 35891.1945 | Suspended Ceiling Tile - Metal Total | 2.5 | 2
A | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Mineral fibre suspended ceiling tiles 600 x 1200
Mineral fibre suspended ceiling tiles 600 x 600 Total | 83 | 7.494 | 0 | 19956.3759 | 15934.8186 | 0 | 0 | 35891.1945 | MODERATE | 3 | 2
Suspended Ceiling Tile - Metal | [8 empty] | Mineral fibre suspended ceiling tiles 600 x 1200 Total | 3 | 2
B | 10 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | Bulkhead (tiles)
C | 2 | 2.5 | 0 | 134 | 670 | 0 | 0 | 804 | MODERATE | 3 | 2
A | 3 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | Bulkhead (tiles) Total | 3 | 2
Suspended Ceiling Tile - Metal Total | 15 | 13.4667 | 0 | 134 | 670 | 0 | 0 | 804 | Ceiling Finishes Total | 2.6829 | 2
Exposed underside of stair | [8 empty] | Comfort Cooling
B | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Computer room air conditioning
Exposed underside of stair Total | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Exposed Concrete | [8 empty] | Computer room air conditioning Total | 2 | 2
A | 8 | 57.5 | 0 | 0 | 0 | 0 | 0 | 0 | Comfort Cooling Total | 2 | 2
Exposed Concrete Total | 8 | 57.5 | 0 | 0 | 0 | 0 | 0 | 0 | Cubicles
Mineral fibre suspended ceiling tiles 600 x 1200 | [8 empty] | High Pressure Laminated Chipboard
B | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
C | 3 | 2 | 0 | 5811.72 | 0 | 0 | 0 | 5811.72 | LOW | 2 | 2
Mineral fibre suspended ceiling tiles 600 x 1200 Total | 10 | 7.6 | 0 | 5811.72 | 0 | 0 | 0 | 5811.72 | High Pressure Laminated Chipboard Total | 2.75 | 2
Metal suspended ceiling tiles 600x1200 | [8 empty] | Cubicles Total | 2.75 | 2
B | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | Decorations
Metal suspended ceiling tiles 600x1200 Total | 3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to walls
Plasterboard & Skim finish | [8 empty] | MODERATE | 3 | 2
B | 16 | 14.625 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Plasterboard & Skim finish Total | 16 | 14.625 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to walls Total | 2.6111 | 2
Exposed Soffit | [8 empty] | Emulsion paint finish to Ceiling
B | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
A | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | Emulsion paint finish to Ceiling Total | 3 | 2
Exposed Soffit Total | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | Decoration of timber surfaces
Timber boarding | [8 empty] | LOW | 2 | 2
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Decoration of timber surfaces Total | 2 | 2
Timber boarding Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery decorations (architraves, skirting)
MDF Boards | [8 empty] | MODERATE | 3 | 2
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
MDF Boards Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery decorations (architraves, skirting) Total | 2.5 | 2
Bulkhead (tiles) | [8 empty] | Timber surround to rooflight
C | 1 | 2 | 0 | 458.82 | 0 | 0 | 0 | 458.82 | LOW | 2 | 2
Bulkhead (tiles) Total | 1 | 2 | 0 | 458.82 | 0 | 0 | 0 | 458.82 | Timber surround to rooflight Total | 2 | 2
Ceiling Finishes Total | 142 | 12.4789 | 0 | 26360.9159 | 16604.8186 | 0 | 0 | 42965.7345 | Door decorations (internal)
Cold Water Plant & Equipment | [8 empty] | LOW | 2 | 2
Cold Water Storage Tanks | [8 empty] | Door decorations (internal) Total | 2 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Paint
Cold Water Storage Tanks Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Cold Water Plant & Equipment Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Paint Total | 2 | 2
Comfort Cooling | [8 empty] | Decorations Total | 2.5571 | 2
Refrigerant pipework systems | [8 empty] | Door
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Solid veneer faced timber door (Single) with vision panel
Refrigerant pipework systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Condensate pipework system | [8 empty] | Solid veneer faced timber door (Single) with vision panel Total | 3 | 2
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Fire door furniture
Condensate pipework system Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | SIGNIFICANT | 4 | 3
Computer room air conditioning | [8 empty] | Fire door furniture Total | 4 | 3
C | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | Door Total | 3.5 | 2.5
Computer room air conditioning Total | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | FF&E
Comfort Cooling Total | 5 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000 | Blinds
Communication System | [8 empty] | MODERATE | 3 | 2
Television and satellite systems | [8 empty] | Blinds Total | 3 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | FF&E Total | 3 | 2
Television and satellite systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Floor Finishes
Communication systems | [8 empty] | Carpet Tile
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Communication systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Public address systems | [8 empty] | Carpet Tile Total | 2.9062 | 2
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Barrier Matting
Public address systems Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Communication System Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | Barrier Matting Total | 3 | 2
Cubicles | [8 empty] | Vinyl tiles
High Pressure Laminated Chipboard | [8 empty] | MODERATE | 3 | 2
C | 4 | 2 | 0 | 5200 | 0 | 0 | 0 | 5200 | LOW | 2 | 2
High Pressure Laminated Chipboard Total | 4 | 2 | 0 | 5200 | 0 | 0 | 0 | 5200 | Vinyl tiles Total | 2.5 | 2
Timber cubicle door | [8 empty] | Raised access tiles
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | SIGNIFICANT | 3 | 4
Timber cubicle door Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Raised access tiles Total | 3 | 4
Cubicles Total | 5 | 3.2 | 0 | 5200 | 0 | 0 | 0 | 5200 | Sheet Vinyl (slip resistant)
Decorations | [8 empty] | MODERATE | 3 | 2.1667
Emulsion paint finish to walls | [8 empty] | Sheet Vinyl (slip resistant) Total | 3 | 2.1667
B | 63 | 7.746 | 0 | 0 | 0 | 0 | 0 | 0 | Carpet Sheet
C | 54 | 2.7037 | 0 | 1506.0222 | 9448.8264 | 371.7 | 0 | 11326.5486 | MODERATE | 3 | 2
A | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Emulsion paint finish to walls Total | 119 | 5.4286 | 0 | 1506.0222 | 9448.8264 | 371.7 | 0 | 11326.5486 | Carpet Sheet Total | 2.5 | 2
Emulsion paint finish to Ceiling | [8 empty] | Vinyl tile (blistered)
C | 1 | 3 | 0 | 0 | 181.02 | 0 | 0 | 181.02 | MODERATE | 3 | 2
Emulsion paint finish to Ceiling Total | 1 | 3 | 0 | 0 | 181.02 | 0 | 0 | 181.02 | Vinyl tile (blistered) Total | 3 | 2
Decoration of timber surfaces | [8 empty] | Sheet Vinyl
C | 2 | 2.5 | 0 | 14 | 35 | 0 | 0 | 49 | MODERATE | 3 | 2
A | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Decoration of timber surfaces Total | 3 | 3.6667 | 0 | 14 | 35 | 0 | 0 | 49 | Sheet Vinyl Total | 2.5 | 2
Joinery decorations (architraves, skirting) | [8 empty] | Timber boarding (raised floor)
B | 16 | 6.625 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 3
C | 10 | 2.8 | 0 | 49 | 168 | 35 | 0 | 252 | Timber boarding (raised floor) Total | 3 | 3
A | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | Floor Finishes Total | 2.8627 | 2.0784
Joinery decorations (architraves, skirting) Total | 28 | 5.2143 | 0 | 49 | 168 | 35 | 0 | 252 | IPS
Timber surround to rooflight | [8 empty] | High Pressure Laminated Chipboard
C | 1 | 2 | 0 | 10 | 0 | 0 | 0 | 10 | MODERATE | 2.7143 | 2.2857
Timber surround to rooflight Total | 1 | 2 | 0 | 10 | 0 | 0 | 0 | 10 | LOW | 2 | 2
Door decorations (internal) | [8 empty] | High Pressure Laminated Chipboard Total | 2.625 | 2.25
B | 3 | 6.6667 | 0 | 0 | 0 | 0 | 0 | 0 | IPS Total | 2.625 | 2.25
C | 1 | 4 | 0 | 0 | 0 | 39.24 | 0 | 39.24 | Ironmongery
Door decorations (internal) Total | 4 | 6 | 0 | 0 | 0 | 39.24 | 0 | 39.24 | Ironmongery (general item)
Floor Paint | [8 empty] | MODERATE | 3 | 2.75
B | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150 | Ironmongery (general item) Total | 2.5714 | 2.4286
Floor Paint Total | 29 | 7.7931 | 0 | 150 | 0 | 0 | 0 | 150 | Door Lever
Decorations Total | 185 | 5.7189 | 0 | 1729.0222 | 9832.8464 | 445.94 | 0 | 12007.8086 | LOW | 2 | 2
Door | [8 empty] | Door Lever Total | 2 | 2
Solid veneer faced timber door (Single) with vision panel | [8 empty] | Lever handle
B | 32 | 10.125 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
C | 1 | 1 | 100 | 0 | 0 | 0 | 0 | 100 | Lever handle Total | 2 | 2
A | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Door closer
Solid veneer faced timber door (Single) with vision panel Total | 37 | 10.9459 | 100 | 0 | 0 | 0 | 0 | 100 | MODERATE | 3 | 2
Solid veneer faced timber door (Single) | [8 empty] | Door closer Total | 3 | 2
B | 50 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | Pull handles
Solid veneer faced timber door (Single) Total | 50 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Solid veneer faced timber door (Double) with vision panel | [8 empty] | Pull handles Total | 2 | 2
B | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | Ironmongery Total | 2.3125 | 2.1875
Solid veneer faced timber door (Double) with vision panel Total | 6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | Joinery
Hollow core door (Single) | [8 empty] | Timber sub frame / sill / general surfaces
B | 8 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Hollow core door (Single) Total | 8 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | Timber sub frame / sill / general surfaces Total | 3 | 2
Fire door furniture | [8 empty] | Ply boxing
D | 1 | 1 | 25 | 0 | 0 | 0 | 0 | 25 | LOW | 2 | 2
Fire door furniture Total | 1 | 1 | 25 | 0 | 0 | 0 | 0 | 25 | Ply boxing Total | 2 | 2
Aluminium fully glazed door | [8 empty] | Joinery Total | 2.5 | 2
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Mechanical Ventilation
Aluminium fully glazed door Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Centrifugal fans
Glazed Double Leaf | [8 empty] | LOW | 2 | 2
B | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Centrifugal fans Total | 2 | 2
Glazed Double Leaf Total | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Humidifier
Solid veneer faced timber door (Single+Half) with vision panel | [8 empty] | LOW | 2 | 2
B | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | Humidifier Total | 2 | 2
Solid veneer faced timber door (Single+Half) with vision panel Total | 5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | Mechanical Ventilation Total | 2 | 2
Steel security door / cell door | [8 empty] | Sink
B | 15 | 15.3333 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China
A | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Steel security door / cell door Total | 17 | 15.8824 | 0 | 0 | 0 | 0 | 0 | 0 | LOW | 2 | 2
Hollow Core door single (with vision panel) | [8 empty] | Vitreous China Total | 2.8 | 2
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | Stainless Steel
Hollow Core door single (with vision panel) Total | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 3
Door Total | 130 | 11.1077 | 125 | 0 | 0 | 0 | 0 | 125 | Stainless Steel Total | 3 | 3
FF&E | [8 empty] | Sink Total | 2.8333 | 2.1667
Dumb waiter | [8 empty] | Vanity Unit
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | High Pressure Laminated Chipboard
Dumb waiter Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Laminate worktop on metal legs | [8 empty] | LOW | 2 | 2
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | High Pressure Laminated Chipboard Total | 2.8333 | 2
Laminate worktop on metal legs Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Vanity Unit Total | 2.8333 | 2
Blinds | [8 empty] | Wall Finishes
B | 15 | 7.7333 | 0 | 0 | 0 | 0 | 0 | 0 | Plaster on Brick/Block
C | 4 | 2 | 0 | 600 | 0 | 0 | 0 | 600 | MODERATE | 3 | 2
Blinds Total | 19 | 6.5263 | 0 | 600 | 0 | 0 | 0 | 600 | LOW | 2 | 2
Worktop & units | [8 empty] | Plaster on Brick/Block Total | 2.8 | 2
B | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | Hessian wall panels
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | MODERATE | 3 | 2
Worktop & units Total | 3 | 9.6667 | 0 | 0 | 0 | 0 | 0 | 0 | Hessian wall panels Total | 3 | 2
Metal handrail | [8 empty] | Wall Finishes Total | 2.8125 | 2
B | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | WC
Metal handrail Total | 2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China
Benches | [8 empty] | MODERATE | 3 | 2
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Vitreous China Total | 3 | 2
Benches Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | WC Total | 3 | 2
Built in cupboards etc | [8 empty] | Grand Total | 2.6783 | 2.0478
B | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Built in cupboards etc Total | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Timber staircase
B | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Timber staircase Total | 4 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Shelfing
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Shelfing Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Laminated reception desk
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Laminated reception desk Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Reception glazing (aluminium framed)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Reception glazing (aluminium framed) Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted fixed timber seating with metal frame
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted fixed timber seating with metal frame Total | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Vertical
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Vertical Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Drop down
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Grab Rails - Drop down Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Hand Rails
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Hand Rails Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Units
B | 3 | 9.3333 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Units Total | 4 | 10.75 | 0 | 0 | 0 | 0 | 0 | 0
Benching
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Benching Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fixed laminate Worktop / desking
B | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fixed laminate Worktop / desking Total | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen units with laminate worktops
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen units with laminate worktops Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fixed base timber units
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fixed base timber units Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted seat and counter
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Floor mounted seat and counter Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fixed wooden bed (vandalised wooden tops)
B | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fixed wooden bed (vandalised wooden tops) Total | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Dumbwaiter lift
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Dumbwaiter lift Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
FF&E Total | 68 | 9.6029 | 0 | 600 | 0 | 0 | 0 | 600
Floor Finishes
Carpet Tile
B | 25 | 8.32 | 0 | 0 | 0 | 0 | 0 | 0
C | 32 | 2.8438 | 0 | 6422.8204 | 32305.4182 | 0 | 522.96 | 39251.1986
Carpet Tile Total | 57 | 5.2456 | 0 | 6422.8204 | 32305.4182 | 0 | 522.96 | 39251.1986
Barrier Matting
C | 2 | 3 | 0 | 0 | 430.26 | 0 | 0 | 430.26
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Barrier Matting Total | 3 | 8.6667 | 0 | 0 | 430.26 | 0 | 0 | 430.26
Vinyl tiles
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 2 | 3 | 0 | 0 | 328.831 | 0 | 0 | 328.831
Vinyl tiles Total | 3 | 4.6667 | 0 | 0 | 328.831 | 0 | 0 | 328.831
Raised access tiles
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 1 | 30 | 0 | 0 | 0 | 0 | 30
Raised access tiles Total | 3 | 5.6667 | 30 | 0 | 0 | 0 | 0 | 30
Quarry Tiles
B | 9 | 8.8889 | 0 | 0 | 0 | 0 | 0 | 0
Quarry Tiles Total | 9 | 8.8889 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl (slip resistant)
B | 9 | 8.2222 | 0 | 0 | 0 | 0 | 0 | 0
C | 6 | 1.6667 | 440.684 | 2639.058 | 0 | 0 | 0 | 3079.742
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl (slip resistant) Total | 16 | 6.1875 | 440.684 | 2639.058 | 0 | 0 | 0 | 3079.742
Carpet Sheet
C | 2 | 3 | 0 | 0 | 878.3016 | 0 | 0 | 878.3016
Carpet Sheet Total | 2 | 3 | 0 | 0 | 878.3016 | 0 | 0 | 878.3016
Vinyl tile (blistered)
C | 1 | 3 | 0 | 0 | 260 | 0 | 0 | 260
Vinyl tile (blistered) Total | 1 | 3 | 0 | 0 | 260 | 0 | 0 | 260
Ceramic tiles
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Ceramic tiles Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl
C | 4 | 2.5 | 0 | 336.105 | 1059.8511 | 0 | 0 | 1395.9561
A | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Sheet Vinyl Total | 5 | 4 | 0 | 336.105 | 1059.8511 | 0 | 0 | 1395.9561
Concrete
B | 28 | 45.8929 | 0 | 0 | 0 | 0 | 0 | 0
A | 13 | 51.9231 | 0 | 0 | 0 | 0 | 0 | 0
Concrete Total | 41 | 47.8049 | 0 | 0 | 0 | 0 | 0 | 0
Timber boarding (raised floor)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 2 | 0 | 100 | 0 | 0 | 0 | 100
Timber boarding (raised floor) Total | 2 | 7 | 0 | 100 | 0 | 0 | 0 | 100
Floor Finishes Total | 143 | 17.8182 | 470.684 | 9497.9834 | 35262.6619 | 0 | 522.96 | 45754.2893
Fuel Services
Gas distribution pipework
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas distribution pipework Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel shut-off valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel shut-off valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel storage tank.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel storage tank. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fuel Services Total | 4 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Controls
Control Panels
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Control Panels Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Control Valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Control Valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Controls Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution
Heating Distribution Pipework
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution Pipework Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Services thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Services thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Plant Manual Isolation Valves
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Plant Manual Isolation Valves Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Actuators
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Motorised Actuators Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Radiators.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Radiators. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fan Convectors
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fan Convectors Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Natural Convectors
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Natural Convectors Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LTHW Warm air heaters
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LTHW Warm air heaters Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electric Heaters.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electric Heaters. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Distribution Total | 11 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Plant & Auxiliaries
Gas fired boiler 100kw - 300kw
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired boiler 100kw - 300kw Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Flue Systems (stainless steel 200 kw boiler)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Flue Systems (stainless steel 200 kw boiler) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Commercial Circulating Pump (Single or dual type)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Commercial Circulating Pump (Single or dual type) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Air-to-air commercial Heat pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Air-to-air commercial Heat pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Heating Plant & Auxiliaries Total | 4 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Distribution Services
Hot and Cold Water Pipework systems
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot and Cold Water Pipework systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Services thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Services thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Shower mixer and head
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Shower mixer and head Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot & Cold Water Distribution Services Total | 6 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Plant & Equipment
Circulating Pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Circulating Pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired hot water heaters
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Gas fired hot water heaters Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Boilers - (tea points)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Water Boilers - (tea points) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Hot Water Plant & Equipment Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Internal glazing
Softwood Timber
B | 7 | 8.5714 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber Total | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Metal frame
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Metal frame Total | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0
Softwood timber (veneer)
A | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Softwood timber (veneer) Total | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Rooflight with metal frame
B | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Rooflight with metal frame Total | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber (painted)
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Softwood Timber (painted) Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Internal glazing Total | 26 | 10.9231 | 0 | 0 | 0 | 0 | 0 | 0
IPS
High Pressure Laminated Chipboard
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
C | 8 | 2 | 0 | 7150 | 0 | 0 | 0 | 7150
High Pressure Laminated Chipboard Total | 10 | 3.2 | 0 | 7150 | 0 | 0 | 0 | 7150
IPS Total | 10 | 3.2 | 0 | 7150 | 0 | 0 | 0 | 7150
Ironmongery
Ironmongery (general item)
B | 101 | 10.3366 | 0 | 0 | 0 | 0 | 0 | 0
C | 7 | 2.4286 | 0 | 475 | 205 | 0 | 0 | 680
A | 4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0
Ironmongery (general item) Total | 112 | 10.0982 | 0 | 475 | 205 | 0 | 0 | 680
Door Lever
C | 2 | 2 | 0 | 50 | 0 | 0 | 0 | 50
Door Lever Total | 2 | 2 | 0 | 50 | 0 | 0 | 0 | 50
Lever handle
C | 5 | 2 | 0 | 125 | 0 | 0 | 0 | 125
Lever handle Total | 5 | 2 | 0 | 125 | 0 | 0 | 0 | 125
Door closer
C | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Door closer Total | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Pull handles
C | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Pull handles Total | 1 | 2 | 0 | 25 | 0 | 0 | 0 | 25
Ironmongery Total | 121 | 9.4959 | 0 | 700 | 205 | 0 | 0 | 905
Joinery
Timber skirting
B | 65 | 8.5538 | 0 | 0 | 0 | 0 | 0 | 0
A | 4 | 15.75 | 0 | 0 | 0 | 0 | 0 | 0
Timber skirting Total | 69 | 8.971 | 0 | 0 | 0 | 0 | 0 | 0
Timber dado / picture rail
B | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber dado / picture rail Total | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber / MDF architraves
B | 93 | 9.8495 | 0 | 0 | 0 | 0 | 0 | 0
A | 4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0
Timber / MDF architraves Total | 97 | 10.1649 | 0 | 0 | 0 | 0 | 0 | 0
Timber sub frame / sill / general surfaces
B | 24 | 8.1667 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 3 | 0 | 0 | 50 | 0 | 0 | 50
Timber sub frame / sill / general surfaces Total | 25 | 7.96 | 0 | 0 | 50 | 0 | 0 | 50
Ply boxing
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Ply boxing Total | 2 | 6 | 0 | 150 | 0 | 0 | 0 | 150
Timber deck
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber deck Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
MDF / Ply panels above window
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
MDF / Ply panels above window Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Panelling to radiator
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Panelling to radiator Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber surround to rooflight
B | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Timber surround to rooflight Total | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Metal joinery
B | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Metal joinery Total | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Joinery Total | 222 | 9.2613 | 0 | 150 | 50 | 0 | 0 | 200
Lifting Equipment
Lift Plant & Controls
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lift Plant & Controls Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lifting Equipment Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting Systems
Emergency lighting (inc key switch)
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Emergency lighting (inc key switch) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (internal)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (internal) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (external)
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting and luminaires (external) Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Lighting Systems Total | 7 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mains Power Supplies
LV switchgear (internal)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
LV switchgear (internal) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Main supply switchgear
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Main supply switchgear Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
SWA mains/sub distribution cables.
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
SWA mains/sub distribution cables. Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Earth bonding (Primary)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Earth bonding (Primary) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electricity Meter & Measurement
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Electricity Meter & Measurement Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mains Power Supplies Total | 5 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Ventilation
Packaged Air handling units
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Packaged Air handling units Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Galvanised Ductwork Systems
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Galvanised Ductwork Systems Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Centrifugal fans
C | 1 | 5 | 0 | 0 | 0 | 0 | 1000 | 1000
Centrifugal fans Total | 1 | 5 | 0 | 0 | 0 | 0 | 1000 | 1000
Ductwork thermal insulation
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Ductwork thermal insulation Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
External louvres steel painted
B | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
External louvres steel painted Total | 2 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Humidifier
C | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000
Humidifier Total | 1 | 1 | 10000 | 0 | 0 | 0 | 0 | 10000
Kitchen Extract canopies/ Hoods (average)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Kitchen Extract canopies/ Hoods (average) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Local extract fans
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Local extract fans Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fire Dampers
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fire Dampers Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Grilles and diffusers
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Grilles and diffusers Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Mechanical Ventilation Total | 13 | 3 | 10000 | 0 | 0 | 0 | 1000 | 11000
Miscellaneous Electrical Equipment & Plant
Kitchen (cooking and support systems)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Kitchen (cooking and support systems) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Electrical Equipment & Plant Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Mechanical Equipment & Plant
Petrol & Diesel Storage and Pumps
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Petrol & Diesel Storage and Pumps Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous Mechanical Equipment & Plant Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Other
Showers
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Showers Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Metal shower
B | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Metal shower Total | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Other Total | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Power Generation
Standby generator plus prime mover
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Standby generator plus prime mover Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Power Generation Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sink
Cleaners sink (Belfast etc)
B | 4 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0
Cleaners sink (Belfast etc) Total | 4 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0
Vitreous China
B | 7 | 8.2857 | 0 | 0 | 0 | 0 | 0 | 0
C | 5 | 2 | 0 | 3761.42 | 0 | 0 | 0 | 3761.42
Vitreous China Total | 12 | 5.6667 | 0 | 3761.42 | 0 | 0 | 0 | 3761.42
Stainless Steel
B | 3 | 9.3333 | 0 | 0 | 0 | 0 | 0 | 0
D | 1 | 1 | 100 | 0 | 0 | 0 | 0 | 100
Stainless Steel Total | 4 | 7.25 | 100 | 0 | 0 | 0 | 0 | 100
Sink Total | 20 | 7.1 | 100 | 3761.42 | 0 | 0 | 0 | 3861.42
Sub-Main Distribution
Sub distribution wiring and containment systems
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sub distribution wiring and containment systems Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fixed appliance power supplies/ isolators (Spurs)
B | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Fixed appliance power supplies/ isolators (Spurs) Total | 3 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (critical)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (critical) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (Non critical)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Distribution boards (Non critical) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Switched socket outlet (SSO)
B | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Switched socket outlet (SSO) Total | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Sub-Main Distribution Total | 9 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0
Urinal
Vitreous China
B | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Vitreous China Total | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Urinal Total | 4 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0
Vanity Unit
High Pressure Laminated Chipboard
B | 3 | 7.3333 | 0 | 0 | 0 | 0 | 0 | 0
C | 6 | 2 | 0 | 3900 | 0 | 0 | 0 | 3900
High Pressure Laminated Chipboard Total | 9 | 3.7778 | 0 | 3900 | 0 | 0 | 0 | 3900
Vanity Unit Total | 9 | 3.7778 | 0 | 3900 | 0 | 0 | 0 | 3900
Wall Finishes
Plaster on Brick/Block
B | 107 | 12.1402 | 0 | 0 | 0 | 0 | 0 | 0
C | 15 | 2.2 | 0 | 622.688 | 406.87 | 0 | 0 | 1029.558
A | 4 | 25 | 0 | 0 | 0 | 0 | 0 | 0
Plaster on Brick/Block Total | 126 | 11.3651 | 0 | 622.688 | 406.87 | 0 | 0 | 1029.558
Ceramic Wall Tiles
B | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 0
Ceramic Wall Tiles Total | 14 | 14.5714 | 0 | 0 | 0 | 0 | 0 | 0
Metal / timber stud with plasterboard
B | 4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0
Metal / timber stud with plasterboard Total | 4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0
Pre-finished panels
B | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Pre-finished panels Total | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0
Exposed Concrete
B | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0
A | 7 | 57.8571 | 0 | 0 | 0 | 0 | 0 | 0
Exposed Concrete Total | 9 | 46.7778 | 0 | 0 | 0 | 0 | 0 | 0
Brickwork
B | 18 | 40 | 0 | 0 | 0 | 0 | 0 | 0
A | 15 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Brickwork Total | 33 | 46.8182 | 0 | 0 | 0 | 0 | 0 | 0
Hessian wall panels
C | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Hessian wall panels Total | 1 | 2 | 0 | 150 | 0 | 0 | 0 | 150
Glazed partitions
B | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
A | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Glazed partitions Total | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Acoustic Wall Panels
B | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Acoustic Wall Panels Total | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Metal wall panels
B | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Metal wall panels Total | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0
Blockwork
A | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Blockwork Total | 3 | 55 | 0 | 0 | 0 | 0 | 0 | 0
Wall Finishes Total | 196 | 19.9235 | 0 | 772.688 | 406.87 | 0 | 0 | 1179.558
WC
Vitreous China
B | 25 | 8.64 | 0 | 0 | 0 | 0 | 0 | 0
C | 1 | 3 | 0 | 0 | 615.82 | 0 | 0 | 615.82
Vitreous China Total | 26 | 8.4231 | 0 | 0 | 615.82 | 0 | 0 | 615.82
WC Total | 26 | 8.4231 | 0 | 0 | 615.82 | 0 | 0 | 615.82
#N/A
#N/A
(blank) |  |  | 0 | 0 | 0 | 0 | 0 | 0
#N/A Total |  |  | 0 | 0 | 0 | 0 | 0 | 0
#N/A Total |  |  | 0 | 0 | 0 | 0 | 0 | 0
Grand Total | 1390 | 11.7188 | 20695.684 | 59822.0295 | 62978.0169 | 445.94 | 1522.96 | 145464.6304
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Fabric Survey
Condition Ranking | [9 empty] | Priority |  |  | Type
A |  |  | A = Good - Performing as intended and operating efficiently | [6 empty] | 1 | Urgent |  | E | Environmental
B |  |  | B = Satisfactory - performing as intended, exhibiting minor deterioration. | [6 empty] | 2 | within 2 years |  | F | Fire Precaution
C |  |  | C = Poor - exhibiting major defects and/or not operating as intended. | [6 empty] | 3 | 3 to 5 years |  | G | Consequential risk
D |  |  | D = Failed - life expired and/or serious risk imminent failure | [6 empty] | 4 | 5 to 10 years |  | H | Health and Safety
[10 empty] | 5 | 10 to 15 years |  | I | Further Investigation
[10 empty] | 6 | 15 to 25 years |  | L | Loss of Service
[13 empty] | Q | Energy
[13 empty] | R | Recommendation
[13 empty] | S | Security
ROOM DESCRIPTION |  |  |  | ROOM FABRIC | [5 empty] | CONDITION SURVEY
Internal / External | Building | Room No. / Name | Floor | Element | Element | Element group | Element group | Sub element group | Sub element group | Unit rate | Item quantity | Standard Rate | CONDITION RANK | PRIORITY | TYPE | Typical Life from new (YEARS) | Estimated Remaining Useful Design Life (YEARS) | Cost | Disrepair Narrative / General Comments | Remedial Works | Photo ref: (Applied to "C" or "D" ratings i.e.. Cx or Dx) | Current & Impending Backlog Risk Assessment |  | SCORE RANGE | RISK RANKING | PREDICTED REPLACEMENT (Years) | [5 empty] | Total | General Comments
[24 empty] | 1 - 5 | Low | 1 | 1-2 | 3-5 | 5-10 | 10-15 | 15-25 |  | Remedial Works
[24 empty] | 11 - 15 | Significant | [7 empty] | Remedial Works
[21 empty] | Photo ref: (Applied to "C" or "D" ratings i.e.. Cx or Dx) | #REF! | #REF! | SCORE RANGE | RISK RANKING | Priority 1 - 2018/19 | Priority 2 - 2019/20 | Priority 3 - 2021/23 | Priority 4 - 2023/28 | Priority 5 - 2028/33 | Priority 6 - 2033/42 |  | General Comments
External Areas | 1 | External | 0 |  | Fencing | Fencing & Gates | Fencing & Security |  | Timber boards | m | 10 | 106.5 | D | 1 | S | 15 | Urgent | 1065 | No security to site where fence panels have blown down adjacent to 063BR, cost included but maybe adjoining owners responsibility | Replace damaged fence panels and posts | N/A |  |  |  |  | 1065 | [5 empty] | 1065
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Tarmacadam | m2 | 30 | 120 | B | 2 | R | 20 | Within 2 years | 3600 | Foot paths too narrow to allow wheelchairs or persons with mobility aids o pass. | Form passing places along footpaths to allow occupants to pass without moving on to grassed areas. | N/A | [5 empty] | 3600 |  |  |  |  | 3600
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Tarmacadam | m2 | 30 | 120 | A | 6 | R | 20 | 20 | 3600 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 3600 | 3600
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Tarmacadam | m2 | 300 | 66 | B | 4 | R | 20 | 20 | 19800 | Pot holes and general breakdown of tarmac surface in places. | Scarify and resurface car park | N/A | [7 empty] | 19800 |  |  | 19800
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Tarmacadam | m2 | 140 | 120 | B | 6 | R | 20 | 15-25 years | 16800 | Tarmac footpaths around the site good condition, leaf litter only | Renew | N/A | [9 empty] | 16800 | 16800
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Paving slabs | m2 | 160 | 120 | C | 2 | R | 20 | within 2 years | 19200 | Paving slabbed areas around the site, some uneven, large open gaps, trip hazards etc | Uplift slabs, construct base, lay tarmac | N/A | [5 empty] | 19200 |  |  |  |  | 19200
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Brick paving | m2 | 30 | 240 | C | 2 | H | 20 | Within 2 years | 7200 | Main entrance has no handrails to slope, poor contrast with blue bricks, which have the potential to be slippery in the wet. | Uplift ramp install new ramp with landing, slope and handrails | N/A | [5 empty] | 7200 |  |  |  |  | 7200
External Areas | 1 | External | 0 |  | Ramps & Steps | Fencing & Gates | Ballustrades & handrails |  | Metal handrails | m | 30 | 240 | C | 2 | H | 20 | Within 2 years | 7200 | Exit doors and ramps often with no handrails | Install suitable and sufficient handrails to each egress door. | N/A | [5 empty] | 7200 |  |  |  |  | 7200
External Areas | 1 | External | 0 |  | Ramps & Steps | Fencing & Gates | Ballustrades & handrails |  | Metal handrails | m | 30 | 240 | A | 6 | H | 20 | 20 | 7200 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 7200 | 7200
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roofs - pitched |  | Concrete tiles | m2 | 1575 | 143 | B | 5 | G | 40 | 10-15 years | 225225 | Existing concrrete interlocking tiles appears weatherproof but now nearing the end of useable life. Pathch repairs evident on numerous pitches. | Allow to remove and refit concrete interlocking tiles to pitched roofs and renew including new insulation. | N/A | [8 empty] | 225225 |  | 225225
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roofs - flat |  | Mineral felt | m2 | 200 | 160 | A | 6 | G | 20 | 15-25 years | 32000 | Existing covering is mineral felt and appears recently installed. | Remove then allow for cut to falls insulation and mineral felt. | N/A | [9 empty] | 32000 | 32000
External Areas | 1 | External | 0 |  | External Landscaping | Fencing & Gates | Hard Landscaping |  | Tarmacadam | m2 | 250 | 66 | B | 4 | R | 20 | 5-10 years | 16500 | Car park has some potholes, part tarmac repairs, no disable bay markings, some areas of tarmac nearing end of life. | Scarify and overlay car park and mark dedicated ambulance and disabled bays | N/A | [7 empty] | 16500 |  |  | 16500
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roof Drainage |  | PVC Gutters & Downpipes | m | 175 | 96 | A | 6 | G | 25 | 15-25 years | 16800 | Gutters to mono pitched roofs are concrete sectional box gutters. Have been relined with felt as a retrospective repair, some leaking evident. | Reline with a cold applied liquid gutter lining system e.g Sika | N/A | [9 empty] | 16800 | 16800
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Roof lights |  | Propriety Unit | Nr | 16 | 1107 | B | 6 | G | 25 | 15-25 years | 17712 | Recently installed | Renew in conjunction with roof recover | N/A | [9 empty] | 17712 | 17712
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Wall structure |  | Brickwork | m2 | 0 | 0 | B | 6 | G | 40 | 15-25 years | 0 | 2 courses of blue bricks with clay brickwork above. Typical minor weathering, ivy scars, staining, fine thermal cracks and erosion of mortar. | No repairs required. | N/A | [9 empty] | 0 | 0
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Doors |  | PVCu Doors | Nr | 1 | 4821 | B | 2 | S | 30 | Within 2 years | 4821 | Existing PVCu double doorsets to the main entrance | Recommend replacement with powder coated aluminium automatic sliding door to aid ambulance crews and persons with mobility aids. Price uplifted for automation | N/A | [5 empty] | 4821 |  |  |  |  | 4821
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Windows |  | PVCu windows | m2 | 125 | 767 | B | 6 | S | 35 | 15-25 years | 95875 | Existing windows throughout the site are PVCu double glazed, Good Condition. | Replace | N/A | [9 empty] | 95875 | 95875
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Doors |  | PVCu Doors | Nr | 6 | 3821 | B | 6 | S | 30 | 15-25 years | 22926 | Existing PVCu double doorsets throughout the site are PVCu double glazed | Recommend replacement with powder coated aluminium for durability with escape furniture | N/A | [9 empty] | 22926 | 22926
External | 1 | External | 0 |  | Building Superstructure | Fencing & Gates | Doors |  | PVCu Doors | Nr | 10 | 1878 | B | 6 | S | 30 | 15-25 years | 18780 | Existing PVCu single doorsets throughout the site are PVCu double glazed. Final exit doors have no contrast to panic furniture | Renew doorsets with powder coated aluminium with escape furniture | N/A | [9 empty] | 18780 | 18780
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 202 | 11 | B | 3 | E | 5 | 3-5 years | 2222 | Paint to ceiling, generally good condition | Redecorate | [7 empty] | 2222 |  |  |  | 2222
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 202 | 11 | A | 4 | E | 5 | 5-10 years | 2222 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 2222 |  |  | 2222
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 202 | 11 | A | 5 | E | 5 | 10-15 years | 2222 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 2222 |  | 2222
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 202 | 11 | A | 6 | E | 5 | 15-25 years | 2222 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 2222 | 2222
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 388 | 11.29 | B | 3 | E | 5 | 3-5 years | 4380.52 | Wallpaper, generally good condition | Redecorate | [7 empty] | 4380.52 |  |  |  | 4380.52
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 388 | 11.29 | A | 4 | E | 5 | 5-10 years | 4380.52 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 4380.52 |  |  | 4380.52
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 388 | 11.29 | A | 5 | E | 5 | 10-15 years | 4380.52 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 4380.52 |  | 4380.52
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper | m2 | 388 | 11.29 | A | 6 | E | 5 | 15-25 years | 4380.52 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 4380.52 | 4380.52
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet | m2 | 202 | 59 | B | 4 | E | 15 | 5-10 years | 11918 | Generally good condition | Renew | [8 empty] | 11918 |  |  | 11918
Internal | 1 | Dining Room / Living Rooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet | m2 | 202 | 59 | A | 6 | E | 15 | 15-25 years | 11918 | Cyclical replacement | Cyclical replacement | [10 empty] | 11918 | 11918
Internal | 1 | Dining Room / Living Rooms | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Nr | 3 | 1183 | B | 6 | F | 25 | 15-25 years | 3549 | Double doorsets, good condition | Renew | [10 empty] | 3549 | 3549
Internal | 1 | Dining Room / Living Rooms | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Nr | 4 | 931 | B | 6 | F | 25 | 15-25 years | 3724 | Single doorsets, good condition | Renew | [10 empty] | 3724 | 3724
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 274 | 11 | B | 3 | E | 5 | 3-5 years | 3014 | Paint to ceiling, generally good condition | Redecorate | [7 empty] | 3014 |  |  |  | 3014
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 274 | 11 | A | 4 | E | 5 | 5-10 years | 3014 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 3014 |  |  | 3014
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 274 | 11 | A | 5 | E | 5 | 10-15 years | 3014 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 3014 |  | 3014
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 274 | 11 | A | 6 | E | 5 | 20-25 years | 3014 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 3014 | 3014
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 420 | 11.29 | B | 3 | E | 5 | 3-5 years | 4741.8 | Good condition | Redecorate | [7 empty] | 4741.8 |  |  |  | 4741.8
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 420 | 11.29 | A | 4 | E | 5 | 5-10 years | 4741.8 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 4741.8 |  |  | 4741.8
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 420 | 11.29 | A | 5 | E | 5 | 10-15years | 4741.8 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 4741.8 |  | 4741.8
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to walls | m2 | 420 | 11.29 | A | 6 | E | 5 | 15-25 years | 4741.8 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 4741.8 | 4741.8
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Floor finishes |  | Carpet | m2 | 274 | 59 | B | 4 | E | 15 | 5-10 years | 16166 | Generally good condition | Renew | [8 empty] | 16166 |  |  | 16166
Internal | 1 | Circulation Areas | 0 |  | Internal finishes |  | Floor finishes |  | Carpet | m2 | 274 | 59 | A | 6 | E | 15 | 15-25 years | 16166 | Cyclical replacement | Cyclical replacement | [10 empty] | 16166 | 16166
Internal | 2 | Circulation Areas | 0 |  | Balustrades & handrails |  | Timber handrails |  | Timber | lm | 250 | 94 | B | 5 | E | 20 | 10-15years | 23500 | Generally good condition | Renew | [9 empty] | 23500 |  | 23500
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 65 | 11 | B | 3 | H | 5 | 3-5 years | 715 | Paint to ceiling, generally good condition | Redecorate | [7 empty] | 715 |  |  |  | 715
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 65 | 11 | A | 4 | H | 5 | 5-10 years | 715 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 715 |  |  | 715
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 65 | 11 | A | 5 | H | 5 | 10-15 years | 715 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 715 |  | 715
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 65 | 11 | A | 6 | H | 5 | 15-25 years | 715 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 715 | 715
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 30 | 11 | B | 3 | H | 5 | 3-5 years | 330 | Good condition | Redecorate | [7 empty] | 330 |  |  |  | 330
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 30 | 11 | A | 4 | H | 5 | 5-10 years | 330 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 330 |  |  | 330
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 30 | 11 | A | 5 | H | 5 | 10-15 years | 330 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 330 |  | 330
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 30 | 11 | A | 6 | H | 5 | 15-25 years | 330 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 330 | 330
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Wall finishes |  | Ceramic tiling | m2 | 78 | 234 | B | 4 | H | 25 | 5-10 years | 18252 | Tiles, generally good condition, regrouting required every 5 years | Regrout periodically | [8 empty] | 18252 |  |  | 18252
within 2 years | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 65 | 80 | C | 2 | H | 15 | within 2 years | 5200 | Open splits to vinyl welds | Renew | [6 empty] | 5200 |  |  |  |  | 5200
Internal | 1 | Kitchen / Kitchenettes | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 65 | 80 | A | 6 | H | 15 | 15-25 years | 5200 | Cyclical replacement | Cyclical replacement | [10 empty] | 5200 | 5200
Internal | 1 | Kitchen / Kitchenettes | 0 |  | FF&E | FF&E | FF&E |  | Worktop & Units | Item | 4 | 2510 | A | 6 | H | 20 | 15-25 years | 10040 | Good condition, recently refurbished | Renew | [10 empty] | 10040 | 10040
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 3 | H | 5 | 3-5 years | 440 | Paint to ceiling, generally good condition | Redecorate | [7 empty] | 440 |  |  |  | 440
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 4 | H | 5 | 5-10 years | 440 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 440 |  |  | 440
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 5 | H | 5 | 10-15 years | 440 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 440 |  | 440
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 40 | 11 | A | 6 | H | 5 | 15-25 years | 440 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 440 | 440
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Wall finishes |  | Ceramic tiling | m2 | 96 | 234 | A | 6 | H | 25 | 15-25 years | 22464 | Ceramic tiles good condition, recently refurbished | Renew | [10 empty] | 22464 | 22464
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 40 | 95 | A | 5 | H | 10 | 10-15 years | 3800 | Good condition, recently refurbished | Renew | [9 empty] | 3800 |  | 3800
Internal | 1 | Toilets | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 40 | 95 | A | 6 | H | 11 | 15-25 years | 3800 | Cyclical replacement | Cyclical replacement | [10 empty] | 3800 | 3800
Internal | 1 | Toilets | 0 |  | Sanitaryware | FF&E | WC |  | Vitreous China | Item | 14 | 1197 | A | 6 | H | 20 | 15-25 years | 16758 | Good condition, recently refurbished | Renew | [10 empty] | 16758 | 16758
Internal | 1 | Toilets | 0 |  | Sanitaryware | FF&E | WHB |  | Vitreous China | Item | 14 | 525 | A | 6 | H | 21 | 15-25 years | 7350 | Good condition, recently refurbished | Renew | [10 empty] | 7350 | 7350
Internal | 1 | Toilets | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) | Item | 14 | 391 | B | 5 | H | 25 | 10-15 years | 5474 | Appears good condition. Toilet doors do not have own distinguishing colour. | Renew | [9 empty] | 5474 |  | 5474
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 42 | 11 | A | 3 | H | 5 | 3-5 years | 462 | Good condition, recently refurbished | Redecorate | [7 empty] | 462 |  |  |  | 462
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 42 | 11 | A | 4 | H | 5 | 5-10 years | 462 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 462 |  |  | 462
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 42 | 11 | A | 5 | H | 5 | 10-15 years | 462 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 462 |  | 462
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 42 | 11 | A | 6 | H | 5 | 15-25 years | 462 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 462 | 462
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Wall finishes |  | Ceramic tiling | m2 | 98 | 11 | A | 6 | H | 5 | 3-5 years | 1078 | Ceramic tiles good condition, recently refurbished | Renew | [10 empty] | 1078 | 1078
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 42 | 95 | A | 5 | H | 10 | 10-15 years | 3990 | Good condition, recently refurbished | Renew | [9 empty] | 3990 |  | 3990
Internal | 1 | Bath / shower rooms | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 42 | 95 | A | 6 | H | 11 | 15-25 years | 3990 | Good condition, recently refurbished | Renew | [10 empty] | 3990 | 3990
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | WHB |  | Vitreous China | Item | 4 | 525 | A | 6 | H | 20 | 3-5 years | 2100 | In bathrooms - Generally fair condition | [11 empty] | 2100 | 2100
Internal | 1 | Bath / shower rooms | 0 |  | Sanitaryware | FF&E | Bath |  | Height adjustable bath | Item | 4 | 7500 | A | 6 | H | 15 | 15-25 years | 30000 | Good condition, recently refurbished | Renew | [10 empty] | 30000 | 30000
Internal | 1 | Bath / shower rooms | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) | Item | 5 | 391 | B | 5 | H | 25 | 10-15 years | 1955 | Appears generally good condition. Bathroom doors do not have own distinguishing colour. | Renew | [9 empty] | 1955 |  | 1955
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 425 | 11 | B | 3 | E | 5 | 3-5 years | 4675 | Paint to ceiling, good condition | [8 empty] | 4675 |  |  |  | 4675
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 425 | 11 | A | 4 | E | 5 | 5-10 years | 4675 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 4675 |  |  | 4675
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 425 | 11 | A | 5 | E | 5 | 10-15 years | 4675 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 4675 |  | 4675
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 425 | 11 | A | 6 | E | 5 | 15-25 years | 4675 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 4675 | 4675
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper to walls | m2 | 870 | 11 | B | 3 | E | 5 | 3-5 years | 9570 | Good condition | Redecorate | [7 empty] | 9570 |  |  |  | 9570
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper to walls | m2 | 870 | 11 | A | 4 | E | 5 | 5-10 years | 9570 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 9570 |  |  | 9570
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper to walls | m2 | 870 | 11 | A | 5 | E | 5 | 10-15 years | 9570 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 9570 |  | 9570
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Decorations |  | Wallpaper to walls | m2 | 870 | 11 | A | 6 | E | 5 | 15-25 years | 9570 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 9570 | 9570
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet | m2 | 425 | 59 | B | 4 | E | 10 | 10-15 years | 25075 | Generally good condition | [9 empty] | 25075 |  |  | 25075
Internal | 1 | Bedrooms | 0 |  | Internal finishes |  | Floor finishes |  | Carpet | m2 | 425 | 59 | A | 6 | E | 10 | 15-25 years | 25075 | Cyclical replacement | Cyclical replacement | [10 empty] | 25075 | 25075
Internal | 1 | Bedrooms | 0 |  | Sanitaryware | FF&E | WHB |  | Vitreous China | Item | 40 | 525 | B | 3 | E | 20 | 3-5 years | 21000 | Generally fair condition | [8 empty] | 21000 |  |  |  | 21000
Internal | 1 | Bedrooms | 0 |  | Sanitaryware | FF&E | WHB |  | Vitreous China | Item | 40 | 525 | A | 6 | E | 20 | 15-25 years | 21000 | Cyclical replacement | Cyclical replacement | [10 empty] | 21000 | 21000
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 23 | 11 | B | 3 | E | 5 | 3-5 years | 253 | Generally good condition | Redecorate | N/A | [6 empty] | 253 |  |  |  | 253
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 23 | 11 | A | 4 | E | 5 | 5-10 years | 253 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 253 |  |  | 253
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 23 | 11 | A | 5 | E | 5 | 10-15 years | 253 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 253 |  | 253
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 23 | 11 | A | 6 | E | 5 | 15-25 years | 253 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 253 | 253
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 68 | 11 | B | 3 | E | 5 | 3-5 years | 748 | Generally good condition | Redecorate | N/A | [6 empty] | 748 |  |  |  | 748
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 68 | 11 | A | 4 | E | 5 | 5-10 years | 748 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 748 |  |  | 748
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 68 | 11 | A | 5 | E | 5 | 10-15 years | 748 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 748 |  | 748
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 68 | 11 | A | 6 | E | 5 | 15-25 years | 748 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 748 | 748
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 23 | 95 | B | 3 | E | 10 | 3-5 years | 2185 | Generally good condition | Replace | N/A | [6 empty] | 2185 |  |  |  | 2185
Internal | 1 | Laundry | 0 |  | Internal finishes |  | Floor finishes |  | Sheet vinyl | m2 | 23 | 95 | A | 6 | E | 10 | 15-25 years | 2185 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 2185 | 2185
Internal | 1 | Laundry | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 1 | 931 | B | 5 | E | 25 | 10-15 years | 931 | Generally good condition | Replace | N/A | [8 empty] | 931 |  | 931
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 20 | 11 | B | 3 | E | 5 | 3-5 years | 220 | Generally good condition | Redecorate | N/A | [6 empty] | 220 |  |  |  | 220
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 20 | 11 | A | 4 | E | 5 | 5-10 years | 220 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 220 |  |  | 220
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 20 | 11 | A | 5 | E | 5 | 10-15 years | 220 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 220 |  | 220
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 20 | 11 | A | 6 | E | 5 | 15-25 years | 220 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 220 | 220
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 64 | 11 | B | 3 | E | 5 | 3-5 years | 704 | Generally good condition | Redecorate | N/A | [6 empty] | 704 |  |  |  | 704
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 64 | 11 | A | 4 | E | 5 | 5-10 years | 704 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 704 |  |  | 704
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 64 | 11 | A | 5 | E | 5 | 10-15 years | 704 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 704 |  | 704
Internal | 1 | Office | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 64 | 11 | A | 6 | E | 5 | 15-25 years | 704 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 704 | 704
Internal | 1 | Office | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 20 | 95 | B | 3 | E | 10 | 3-5 years | 1900 | Generally fair condition | Replace | N/A | [6 empty] | 1900 |  |  |  | 1900
Internal | 1 | Office | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 20 | 95 | A | 6 | E | 10 | 15-25 years | 1900 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 1900 | 1900
Internal | 1 | Office | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 1 | 931 | B | 5 | E | 25 | 10-15 years | 931 | Generally good condition | Replace | N/A | [8 empty] | 931 |  | 931
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 31 | 11 | B | 3 | E | 5 | 3-5 years | 341 | Generally good condition | Redecorate | N/A | [6 empty] | 341 |  |  |  | 341
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 31 | 11 | A | 4 | E | 5 | 5-10 years | 341 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 341 |  |  | 341
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 31 | 11 | A | 5 | E | 5 | 10-15 years | 341 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 341 |  | 341
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Emulsion paint to ceiling | m2 | 31 | 11 | A | 6 | E | 5 | 15-25 years | 341 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 341 | 341
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 56 | 11 | B | 3 | E | 5 | 3-5 years | 616 | Generally good condition | Redecorate | N/A | [6 empty] | 616 |  |  |  | 616
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 56 | 11 | A | 4 | E | 5 | 5-10 years | 616 | Cyclical redecorations | Cyclical redecorations | [8 empty] | 616 |  |  | 616
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 56 | 11 | A | 5 | E | 5 | 10-15 years | 616 | Cyclical redecorations | Cyclical redecorations | [9 empty] | 616 |  | 616
Internal | 1 | Storage | 0 |  | Internal finishes |  | Decorations |  | Eggshell paint to walls | m2 | 56 | 11 | A | 6 | E | 5 | 15-25 years | 616 | Cyclical redecorations | Cyclical redecorations | [10 empty] | 616 | 616
Internal | 1 | Storage | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 31 | 95 | B | 3 | E | 10 | 3-5 years | 2945 | Generally fair condition | Replace | N/A | [6 empty] | 2945 |  |  |  | 2945
Internal | 1 | Storage | 0 |  | Internal finishes |  | Floor finishes |  | Carpet Tiles | m2 | 31 | 95 | A | 6 | E | 10 | 20-25 years | 2945 | Cyclical replacement | Cyclical replacement | N/A | [9 empty] | 2945 | 2945
Internal | 1 | Storage | 0 |  | Door | FF&E | Door |  | Solid veneer faced timber door (single) with vision panel | Item | 4 | 931 | B | 5 | E | 25 | 10-15 years | 3724 | Generally good condition | Replace | N/A | [8 empty] | 3724 |  | 3724
Internal | 1 | Electrical Cupboard | 1 |  | Electrical Services |  | Mains Power |  | Mains Supply Switchgear | Unit rate | 1 | 3000 | C | 1 | R | 25 | Urgent | 3000 | Main fuse board is nearing the end of its useful life | Replace the existing fuse board with a modern Panel board and install new cable containment from the service head to the new panel board. | N/A |  |  |  |  | 3000 | [5 empty] | 3000
Internal | 1 | Amenity Area | 1 |  | Electrical Services |  | Sub-mains switchgear |  | Sub distribution wiring and containment systems | Unit rate | 1 | 3000 | C | 1 | R | 25 | Urgent | 3000 | Review the latest test results and identify all defects | Repair the defects identified by the condition report | N/A |  |  |  |  | 3000 | [5 empty] | 3000
Internal | 1 | Circulation areas | 1 |  | Electrical Services |  | Mains Power Supplies |  | SWA mains/sub distribution cables. | Unit rate | 1 | 5000 | C | 2 | R | 25 | within 2 years | 5000 | Replace the existing sub-mains cable supplies to all distribution boards in the building | The existing mains cabling is nearing the end of its useful life and may be short when being reconnected into the new panel board. Cables are already being extended with different colour cables at remote end and the cable should be reinstalled and sized to suit the latest version of BS7671. | N/A | [5 empty] | 5000 |  |  |  |  | 5000
Internal | 1 | Bedrooms | 1 |  | Electrical Services |  | Lighting Systems |  | Emergency lighting (Inc. key switch) | Unit rate | 40 | 200 | D | 1 | R | 5 | Urgent | 8000 | Bedrooms should be provided with an emergency luminaire | Install a recessed anti-panic emergency luminaire with a new key test switch. | N/A |  |  |  |  | 8000 | [5 empty] | 8000
Internal | 1 | Bedrooms | 1 |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (internal) | Unit rate | 40 | 40 | C | 1 | R | 20 | Urgent | 1600 | The existing bedroom pendant luminaire should be provided with a dimmable LED lamp and the general lighting supplemented with additional LED recessed down lighters to provide good light levels | Install new LED luminaires to allow for the residents to be able to read and for nursing staff/doctors to be able to carry out medical examinations in the bed rooms. | N/A |  |  |  |  | 1600 | [5 empty] | 1600
Internal | 1 | Bedrooms | 1 |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (internal) | Unit rate | 40 | 100 | C | 1 | R | 20 | Urgent | 4000 | Provision of table lamps in bedrooms | Place a table lamp in each bedroom | N/A |  |  |  |  | 4000 | [5 empty] | 4000
Internal | 1 | Bedrooms | 1 |  | Electrical Services |  | Lighting Systems |  | Lighting control and management systems | Unit rate | 1 | 3000 | C | 3 | R | 20 | 3 to 5 years | 3000 | Light switches should be replaced with new switches with colour contrast colour plates and new dimmer switches for the pendant luminaire should be installed. | Replace the existing light switches with new switches. | N/A | [6 empty] | 3000 |  |  |  | 3000
Internal | 1 | Bedrooms | 1 |  | Electrical Services |  | Sub-mains switchgear |  | Switched socket outlet (SSO) | Unit rate | 40 | 300 | C | 3 | R | 20 | 3 to 5 years | 12000 | Existing sockets should be raised further off the floor for elderly residents to use easily and the plates should be of a contrast colour to the walls. | Replace the existing small power accessories in the rooms and raise the sockets higher off the floor. | N/A | [6 empty] | 12000 |  |  |  | 12000
Internal | 1 | Bedrooms | 1 |  | Electrical Services |  | Protection Systems |  | Fire Alarm Installations (Inc., call points, sounders and detection) | Unit rate | 1 | 7500 | C | 1 | R | 25 | Urgent | 7500 | The bedrooms to be provided with a new addressable detector with a sounder and a beacon/VAD. | Update the fire alarm system to be in line with BS5839. the fire alarm system with a new addressable system. | N/A |  |  |  |  | 7500 | [5 empty] | 7500
Internal | 1 | Corridor | 1 |  | Electrical Services |  | Lighting Systems |  | Emergency lighting (Inc. key switch) | Unit rate | 1 | 10000 | C | 1 | R | 25 | Urgent | 10000 | The corridors should be provided with illuminated emergency exit signs and installed at all turns and exits from internal rooms. | A review of the current exit signage should be carried out and where the signs do not comply with BS5266, new signs should be installed. | N/A |  |  |  |  | 10000 | [5 empty] | 10000
Internal | 1 | Corridor | 1 |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (internal) | Unit rate | 1 | 12000 | C | 3 | R | 25 | 3 to 5 years | 12000 | The existing corridor and amenity area luminaires should be replaced with new LED luminaires to improve energy efficiency. | Install new LED luminaires. | N/A | [6 empty] | 12000 |  |  |  | 12000
Internal | 1 | Corridor | 1 |  | Electrical Services |  | Lighting Systems |  | Lighting control and management systems | Unit rate | 1 | 5000 | C | 3 | R | 25 | 3 to 5 years | 5000 | The corridor lighting should be provided with a photocell lighting controls to make use of natural daylight. | all corridor lighting controls should be reviewed and where possible automatic lighting controls should be installed in the corridors. | N/A | [6 empty] | 5000 |  |  |  | 5000
Internal | 1 | Corridor | 1 |  | Electrical Services |  | Sub-mains switchgear |  | Switched socket outlet (SSO) | Unit rate | 1 | 5000 | C | 3 | R | 25 | 3 to 5 years | 5000 | Existing small power outlet plates should be of a contrast colour to the walls. | All corridor small power accessories should be replaced with new accessories with a contrasting colour finish to the wall. | N/A | [6 empty] | 5000 |  |  |  | 5000
Internal | 1 | Boiler house BP063 | 1 |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Heating Pressurisation Unit | Unit rate | 2 | 1000 | C | 2 | R | 20 | within 2 years | 2000 | 2 No pressurisation units which are outdated and should be replaced with latest Mikrofill model as per the other boiler houses. | Replace with new Mikrofill pressurisation unit. | N/A | [5 empty] | 2000 |  |  |  |  | 2000
Internal | 1 | Boiler house | 1 |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Dosing Pots | Unit rate | 4 | 200 | D | 1 | R | 15 | Urgent | 800 | No dosing pots installed on heating systems. | Dosing pots to be installed on each heating system | N/A |  |  |  |  | 800 | [5 empty] | 800
Internal | 1 | Boiler house | 1 |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Magnetic Filters | Unit rate | 4 | 200 | D | 1 | R | 10 | Urgent | 800 | Newer boilers have been installed on existing old heating systems. Magnetic filters should be installed to protect boilers/pumps | Magnetic filters to be installed on each heating system | N/A |  |  |  |  | 800 | [5 empty] | 800
Internal | 1 | Boiler house | 1 |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Pressure relief discharges/Tundish | Unit rate | 16 | 125 | D | 1 | H | 20 | Urgent | 2000 | Many of the various pressure relief discharges do not discharge into tundishes but directly onto the floor. This is a health and safety hazard. | All discharges to terminate within a tundish and connected directly to a drain. | N/A |  |  |  |  | 2000 | [5 empty] | 2000
Internal | 1 | Boiler house | 1 |  | Mechanical Services |  | Heating Plant & Auxiliaries |  | Expansion Vessels | Unit rate | 4 | 250 | D | 1 | R | 15 | Urgent | 1000 | Expansion vessels do not appear to have correct number of valves and drain off points. To be reviewed. | Expansion vessels need to be reviewed and valves drain off points installed if required. | N/A |  |  |  |  | 1250 | [5 empty] | 1250
Internal | 1 | Boiler house | 1 |  | Mechanical Services |  | Heating Distribution |  | Heating Services Thermal Insulation | Unit rate | 4 | 350 | D | 1 | Q | 30 | Urgent | 1400 | Heating pipework within boiler houses have no insulation on the majority of pipework. | Install thermal insulation on all heating pipework within boiler houses. | N/A |  |  |  |  | 1750 | [5 empty] | 1750
Internal | 1 | Throughout | 1 |  | Mechanical Services |  | Heating Distribution |  | Heating Distribution Pipework | Unit rate | 1 | 30000 | C | 3 | R | 25 | 3 to 5 years | 30000 | Existing distribution is coming to end of life and is a one pipe heating circuit throughout. | Replace existing one pipe heating distribution system with a new 2 pipe heating distribution system. | N/A | [6 empty] | 30000 |  |  |  | 30000
Internal | 1 | Throughout | 1 |  | Mechanical Services |  | Heating Distribution |  | Radiators | Unit rate | 100 | 500 | C | 3 | R | 20 | 3 to 5 years | 50000 | Existing panel and LST radiators are now at end of life and looking very tired and outdated. | Replace all existing radiators with new LST radiators and thermostatic mixing valves. | N/A | [6 empty] | 50000 |  |  |  | 50000
Internal | 1 | Boiler house | 1 |  | Mechanical Services |  | Heating Controls |  | BMS | Unit rate | 4 | 2500 | C | 3 | R | 20 | 3 to 5 years | 10000 | Existing controls are old and very basic | The existing basic controls should be considered to be replaced with a more energy efficient BMS system to control all heating and hot water systems. | N/A | [6 empty] | 10000 |  |  |  | 10000
Internal | 1 | Boiler house | 1 |  | Mechanical Services |  | Hot Water Plant & Equipment |  | Calorifiers | Unit rate | 4 | 2000 | B | 3 | R | 20 | 3 to 5 years | 8000 | The calorifiers are coming to the end of their life and are no longer manufactured. | We would recommend to look at replacing the existing calorifiers with new more energy efficient models. | N/A | [6 empty] | 8000 |  |  |  | 8000
Internal | 1 | Kitchen | 1 |  | Mechanical Services |  | Mechanical Ventilation |  | Kitchen Extract Canopies and ventilation system. | Unit rate | 1 | 15000 | D | 1 | R | 25 | Urgent | 10000 | There are no kitchen extract canopies currently installed within the kitchen and the ventilation system is not to current standards. | The kitchen is outdated and not to current standards and a kitchen ventilation system and extract canopy should be installed. | N/A |  |  |  |  | 10000 | [5 empty] | 10000
Internal | 1 | Throughout | 1 |  | Mechanical Services |  | Hot & Cold Water Distribution Services |  | Hot and Cold Water Pipework | Unit rate | 1 | 25000 | C | 3 | R | 25 | 3 to 5 years | 25000 | Existing distribution is coming to end of life. | Replace existing hot and cold water distribution system with a new. | N/A | [6 empty] | 25000 |  |  |  | 25000
External | 1 | Walkways/escape routes | G |  | Electrical Services |  | Lighting Systems |  | Lighting and luminaires (external) | Unit rate | 1 | 12500 | C | 2 | R | 20 | within 2 years | 12500 | Around the external walkways there are emergency luminaires over the exit doors but there area areas of walkway with no illumination, general and emergency illumination should be installed especially where there is a change in direction or a very narrow walkway. | Install general external luminaires around the building to illuminate the escape routes, luminaires to be controlled by photocells and provided with 3 hour emergency battery back-up. | N/A | [5 empty] | 12500 |  |  |  |  | 12500
Internal | 1 | Bedroom Corridors | G |  | Electrical Services |  | Communication Services |  | Communication systems | Unit rate | 8 | 300 | C | 3 | R | 25 | 3 to 5 years | 2400 | Wi-Fi access to the internet for all bedrooms | Install 2 No IT/Data cables from the data rack to each of the bedroom corridors and install a Wi-Fi module in each corridor. | N/A | [6 empty] | 2400 |  |  |  | 2400
Internal | 1 | Throughout | G |  | Mechanical Services |  | Heating Distribution |  | Fan Convectors | Unit rate | 7 | 1500 | B | 2 | R | 20 | within 2 years | 10500 | Fan convectors hearing the end of their useful life | replace the existing fan convectors with new units. | N/A | [5 empty] | 10500 |  |  |  |  | 10500
[20 empty] | Priority Totals | [5 empty] | 54765 | 77221 | 223862.32 | 141143.32 | 302962.32 | 456367.32
[30 empty] | Overall Total |  | 1256321.28
Internal
167000
423671.2

## Lookup - Fabric Int
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
CODE | Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | STANDARD RATE | RATE TYPE/ Item, M2, Nr | Cost Notes
10101 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10101 | Suspended Ceiling Tile - Metal | 25 | 134 | m2
10102 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10102 | Mineral fibre suspended ceiling tiles 600 x 600 | 25 | 76.47 | m2 | 1 Man houre and materials from BCIS | Labour set at £23.82/hrs
10103 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10103 | Plasterboard & Skim finish | 35 | 31.9 | m2 | 1 Man houre and materials from BCIS
10104
10105 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10105 | Mineral fibre suspended ceiling tiles 600 x 1200 | 25 | 152.94 | m2 | 1 Man houre and materials from BCIS
10106 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10106 | Exposed Concrete | 85 | 80 | m2
10107 | 1 | Internal Finishes | 101 | Ceiling Finishes | 10107 | Plaster | 35 | x | m2
10108DS | 1 | Internal Finishes | 101 | Ceiling Finishes | 10108DS | Exposed underside of stair | 35 | x | m2
10109 |  | Internal Finishes | 101 | Ceiling Finishes | 10109 | Other 1
10201 | 1 | Internal Finishes | 102 | Wall Finishes | 10201 | Metal / timber stud with plasterboard | 35 | 80 | m2
10202 | 1 | Internal Finishes | 102 | Wall Finishes | 10202 | Blockwork | 85 | 280 | m2
10203 | 1 | Internal Finishes | 102 | Wall Finishes | 10203 | Brickwork | 85 | 265 | m2
10204 | 1 | Internal Finishes | 102 | Wall Finishes | 10204 | Glazed partitions | 30 | TBC | m2
10205 | 1 | Internal Finishes | 102 | Wall Finishes | 10205 | Ceramic Wall Tiles | 35 | 110 | m2 | Hack off and replace with new tiles 200 x 200 including pointing and labour.
10206 | 1 | Internal Finishes | 102 | Wall Finishes | 10206 | Exposed Concrete | 85 | 80 | m2
10207 | 1 | Internal Finishes | 102 | Wall Finishes | 10207 | Plaster on Brick/Block | 35 | 35.38 | m2
10208DS | 1 | Internal Finishes | 102 | Wall Finishes | 10208DS | Pre-finished panels | 25 | x | m2
10301 | 1 | Internal Finishes | 103 | Floor Finishes | 10301 | Sheet Vinyl | 10 | 32.01 | m2 | Labour and mat's from BCIS
10302 | 1 | Internal Finishes | 103 | Floor Finishes | 10302 | Carpet Tile | 15 | 43.58 | m2 | Labour and mat's from BCIS
10303 | 1 | Internal Finishes | 103 | Floor Finishes | 10303 | Carpet Sheet | 15 | 35.02 | m2 | Labour and mat's from BCIS
10304 | 1 | Internal Finishes | 103 | Floor Finishes | 10304 | Concrete | 85 | 80 | m2 | Labour and mat's from BCIS
10305 | 1 | Internal Finishes | 103 | Floor Finishes | 10305 | Quarry Tiles | 15 | 34.3 | m2 | Labour and mat's from BCIS
10306 | 1 | Internal Finishes | 103 | Floor Finishes | 10306 | Sheet Vinyl (slip resistant) | 15 | 42.05 | m2 | Labour and mat's from BCIS
10307 | 1 | Internal Finishes | 103 | Floor Finishes | 10307 | Metal Check Deck | 20 | 24 | m2
10308DS |  | Internal Finishes | 103 | Floor Finishes | 10308DS | Barrier Matting | 20 | 71.71 | m2
10309DS | 1 | Internal Finishes | 103 | Floor Finishes | 10309DS | Vinyl tiles | 15 | 42.05 | m2
10310DS | 1 | Internal Finishes | 103 | Floor Finishes | 10310DS | Raised access tiles | 20 | x | m2
10311 | 1 | Internal Finishes | 103 | Floor Finishes | 10311 | Other | x | x | x
10401 | 1 | Internal Finishes | 104 | Decorations | 10401 | Emulsion paint finish to walls | 5 | 5.31 | m2 | Prepare, 1st coat to previously painted walls. BCIS
10402 | 1 | Internal Finishes | 104 | Decorations | 10402 | Heavy Duty Emulsion Paint Finish | 5 | 7.12 | m2 | Prepare, 1st coat + additional coat to previously painted walls. BCIS
10403 | 1 | Internal Finishes | 104 | Decorations | 10403 | Eggshell paint finish to walls | 5 | 7.12 | m2 | Prepare, 1st coat + additional coat to previously painted walls. BCIS
10404 | 1 | Internal Finishes | 104 | Decorations | 10404 | Decoration to Steel Beams | 7 | 5.13 | m2
10405 | 1 | Internal Finishes | 104 | Decorations | 10405 | Floor Paint | 15 | 25 | m2 | Labour and mat's from BCIS
10406 | 1 | Internal Finishes | 104 | Decorations | 10406 | Emulsion paint finish to Ceiling | 5 | 8.62 | m2 | Labour and mat's from BCIS
10407 | 1 | Internal Finishes | 104 | Decorations | 10407 | Door decorations (internal) | 5 | 6.54 | m2
10408 | 1 | Internal Finishes | 104 | Decorations | 10408 | Decoration of inside window frame | 5 | 5.31 | m2
10409 | 1 | Internal Finishes | 104 | Decorations | 10409 | Joinery decorations (architraves, skirting) | 5 | 7 | m2
10410DS | 1 | Internal Finishes | 104 | Decorations | 10410DS | Decoration of timber surfaces | 5 | 7 | m2
10411 | 1 | Internal Finishes | 104 | Decorations | 10411 | Other 1 | x | x | x
10412 | 1 | Internal Finishes | 104 | Decorations | 10412 | Other 2 | x | x | x
20101 | 2 | Door | 201 | Door | 20101 | Hollow core door (Single) | 20 | 120.73 | Nr
20102 | 2 | Door | 201 | Door | 20102 | Solid veneer faced timber door (Single) | 25 | 157.52 | Nr | Spons page 440
20103 | 2 | Door | 201 | Door | 20103 | Solid veneer faced timber door (Single) with vision panel | 25 | 334 | Nr | Spons page 439
20104 | 2 | Door | 201 | Door | 20104 | Solid veneer faced timber door (Single+Half) | 25 | 445.64 | Nr | Spons page 439
20105 | 2 | Door | 201 | Door | 20105 | Solid veneer faced timber door (Single+Half) with vision panel | 25 | 465.64 | Nr | Spons page 439
20106 | 2 | Door | 201 | Door | 20106 | Solid veneer faced timber door (Double) | 25 | 241.46 | Nr | Spons page 439
20107 | 2 | Door | 201 | Door | 20107 | Solid veneer faced timber door (Double) with vision panel | 25 | 668 | Nr | Spons page 439
20108 | 2 | Door | 201 | Door | 20108 | Glazed Single Leaf | 30 | 140 | Nr
20109 | 2 | Door | 201 | Door | 20109 | Glazed Double Leaf | 30 | 280 | Nr
20110 | 2 | Door | 201 | Door | 20110 | Metal Roller Shutter | 20 | 1309 | Nr | Spons page 444 (3000mm x 1000mmm)
20111 | 2 | Door | 201 | Door | 20111 | Aluminium door with factory applied powder coat finish | 35 | 486 | Nr
20112 | 2 | Door | 201 | Door | 20112 | Steel security door / cell door | 40 | x | x
20113DS | 2 | Door | 201 | Door | 20113DS | Fire door furniture | 25 | x | Item
20114 | 2 | Door | 201 | Door | 20114 | Other 1 | x | x | x
30101 | 3 | Ironmongery | 301 | Ironmongery | 30101 | Ironmongery (general item) | 20 | x | Item
40101 | 4 | Joinery | 401 | Joinery | 40101 | Timber / MDF architraves | 25 | 8.6 | lm
40102 | 4 | Joinery |  | Joinery | 40102 | Timber skirting | 25 | 7 | lm
40103DS | 4 | Joinery |  | Joinery | 40103DS | Timber dado / picture rail | 25 | 7 | lm
40104DS | 4 | Joinery |  | Joinery | 40104DS | Timber sub frame / sill / general surfaces | 25 | 7 | lm
40105DS | 4 | Joinery |  | Joinery | 40105DS | Ply boxing | 25 | 38.4 | m
40105 | 4 | Joinery |  | Joinery | 40105 | Other | x | x | x
50101 | 5 | Sanitary ware | 501 | WC | 50101 | Vitreous China | 20 | 307.91 | Item | Remove and replace with new + labour BCIS
50102 | 5 | Sanitary ware | 501 | WC | 50102 | Stainless Steel | 20 | 473.5 | Item
50201 | 5 | Sanitary ware | 502 | Sink | 50201 | Vitreous China | 20 | 289.34 | Item | Remove and replace with new + labour BCIS
50202 | 5 | Sanitary ware | 502 | Sink | 50202 | Stainless Steel | 20 | 473.5 | Item | Remove and replace with new + labour BCIS
50203 | 5 | Sanitary ware | 502 | Sink | 50203 | Cleaners sink (Belfast etc) | 20 | 307.91 | Nr | Remove and replace with new + labour BCIS
50301 | 5 | Sanitary ware | 503 | Urinal | 50301 | Vitreous China | 15 | 609.85 | Item | Remove and replace with new + labour BCIS
50302 | 5 | Sanitary ware | 503 | Urinal | 50302 | Stainless Steel | 20 | 609.85 | Item | Remove and replace with new + labour BCIS
50401 | 5 | Sanitary ware | 504 | Vanity Unit | 50401 | High Pressure Laminated Chipboard | 20 | 650 | Item |  | http://www.washroomcubicles.co.uk/healthcare-ips-panel-system/
50501 | 5 | Sanitary ware | 505 | Cubicles | 50501 | High Pressure Laminated Chipboard | 20 | 650 | Item
50601 | 5 | Sanitary ware | 506 | IPS | 50601 | High Pressure Laminated Chipboard | 20 | 650 | Item
50701 | 5 | Sanitary ware | 507 | Other | 50701 | Other | x | x | x
60101 | 6 | Windows | 601 | Internal glazing | 60101 | Metal frame | 35 | TBC | Nr
60102 | 6 | Windows | 601 | Internal glazing | 60102 | Softwood Timber | 25 | 50.28 | Nr | Remove and replace with new + labour BCIS
60103 | 6 | Windows | 601 | Internal glazing | 60103 | PVCu Double Glazed Unit | 35 | 350 | Nr
60104 | 6 | Windows | 601 | Internal glazing | 60104 | Other | x | x | x
70101 | 7 | FF&E | 701 | FF&E | 70101 | Grab Rails - Vertical | 20 | 27.41 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70102 | 7 | FF&E | 701 | FF&E | 70102 | Grab Rails - Drop down | 20 | 42.91 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70103 | 7 | FF&E | 701 | FF&E | 70103 | Hand Rails | 20 | 27.41 | Nr | cost per item and labour at £23.82/hrs | Commercial washrooms
70104 | 7 | FF&E | 701 | FF&E | 70104 | Soap dispensers | 10 | 1 | Item
70105 | 7 | FF&E | 701 | FF&E | 70105 | Kitchen Units | 15 | 1 | Item
70106 | 7 | FF&E | 701 | FF&E | 70106 | Paper towel dispensers | x | TBC | Nr
70107 | 7 | FF&E | 701 | FF&E | 70107 | Toilet paper dispensers | x | TBC | Nr
70108 | 7 | FF&E | 701 | FF&E | 70108 | Metal Access Stairs | 25 | Varies | Item
70109DS | 7 | FF&E | 701 | FF&E | 70109DS | Laminate worktop on metal legs | 15 |  | Item
70110DS | 7 | FF&E | 701 | FF&E | 70110DS | Blinds | 15 | x | Item
70111DS | 7 | FF&E | 701 | FF&E | 70111DS | Worktop & units | 15 | x | Item
70112DS | 7 | FF&E | 701 | FF&E | 70112DS | Benches | 20 | x | Item
70113DS | 7 | FF&E | 701 | FF&E | 70113DS | Built in cupboards etc | 20 | x | Item
70114DS | 7 | FF&E | 701 | FF&E | 70114DS | Roller racking | 20 |  | Item
70115DS | 7 | FF&E | 701 | FF&E | 70115DS | Metal handrail | 20 |  | Item
70116DS | 7 | FF&E | 701 | FF&E | 70116DS | Timber staircase | 35 |  | Item
70117 | 7 | FF&E | 701 | FF&E | 70117 | Other | x | x | x

## Lookup - Fabric Ext
CODE | Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | STANDARD RATE | RATE TYPE/ Item, M2, Nr | Cost Notes
10101 | 1 | External Landscaping | 101 | Hard Landscaping | 10101 | Tarmacadam | 20 |  | m2
10102 |  |  |  |  | 10102 | Concrete | 30 |  | m2
10103 |  |  |  |  | 10103 | Block Paving | 30 |  | m2
10104 |  |  |  |  | 10104 | Paving Slabs | 30 |  | m2
10201 |  |  | 102 | Soft Landscaping | 10201 | Shrubs & Bushes | 20 |  | Item
10202 |  |  |  |  | 10202 | Grass | 20 |  | m2
20101 | 2 | Roads and Car Parks | 201 | Roads | 20101 | Tarmacadam | 20 |  | m2
20201 |  |  | 202 | Car Parks | 20201 | Tarmacadam | 20 |  | m2
30101 | 3 | Street Furniture | 301 | Bollards | 30101 | Concrete | 30 |  | Item
30102 |  |  |  |  | 30102 | Brushed Aluminium | 25 |  | Item
30103 |  |  |  |  | 30103 | Mild Steel | 20 |  | Item
30201 |  |  | 302 | Benches | 30201 | Timber | 20 |  | Item
30202 |  |  |  |  | 30202 | GRP | 35 |  | Item
30203 |  |  |  |  | 30203 | Metal | 25 |  | Item
40101 | 4 | Building Superstructure | 401 | Roofs - Pitched | 40101 | Slate tile | 75 |  | m2
40102 |  |  |  |  | 40102 | Concrete Tiles | 40 |  | m2
40103 |  |  |  |  | 40103 | Clay tiles | 65 |  | m2
40104 |  |  |  |  | 40104 | Other |  |  | m2
40201 |  |  | 402 | Roofs - Flat | 40201 | Single Ply Membrane | 25 |  | m2
40202 |  |  |  |  | 40202 | Built up Felt System | 20 |  | m2
40203 |  |  |  |  | 40203 | Other
40301 |  |  | 403 | Roof Drainage | 40301 | Pressed Metal Gutters & Downpipes | 20 |  | lm
40302 |  |  |  |  | 40302 | Cast Iron Gutters & Downpipes | 50 |  | lm
40303 |  |  |  |  | 40303 | PVCu Gutters & Downpipes | 25 |  | lm
40304 |  |  |  |  | 40304 | Aluminium Gutters & Downpipes | 30 |  | lm
40305 |  |  |  |  | 40305 | Clearing of gutters | 5 |  | lm
40401 |  |  | 404 | Roof Lights | 40401 | Aluminium Framed Glazing | 30 |  | Nr
40402 |  |  |  |  | 40402 | Proprietary Unit | 25 |  | Nr
40403 |  |  |  |  | 40403 | Velux Window | 25 |  | Nr
40501 |  |  | 405 | Wall Structure | 40501 | Blockwork | 85 |  | m2
40502 |  |  |  |  | 40502 | Brickwork | 85 |  | m2
40503 |  |  |  |  | 40503 | Steel | 85 |  | m2
40504 |  |  |  |  | 40504 | Concrete | 80 |  | m2
40505 |  |  |  |  | 40505 | Modular | 30 |  | m2
40506 |  |  |  |  | 40506 | Other
40601 |  |  | 406 | Wall Finishes | 40601 | Ceramic Tiles | 25 |  | m2
40602 |  |  |  |  | 40602 | Plaster | 50 |  | m2
40603 |  |  |  |  | 40603 | Timber | 25 |  | m2
40604 |  |  |  |  | 40604 | Render Plaster | 25 |  | m2
40605 |  |  |  |  | 40605 | Proprietary Cladding | 40 |  | m2
40606 |  |  |  |  | 40606 | Glazing Curtain Wall | 60 |  | m2
40607 |  |  |  |  | 40607 | Brickwork | 40 |  | m2
40608 |  |  |  |  | 40608 | Blockwork | 30 |  | m2
40609 |  |  |  |  | 40609 | Aluminium Cladding | 40 |  | m2
40701 |  |  | 407 | Decorations | 40701 | External block / brick | 5
40702 |  |  |  |  | 40702 | Timber doors | 5
40703 |  |  |  |  | 40703 | Timber windows | 5
40704 |  |  |  |  | 40704 | Metal doors | 5
40705 |  |  |  |  | 40705 | Metal windows | 5
40706 |  |  |  |  | 40706 | Emulsion to render | 5
40707 |  |  |  |  | 40707 | cast iron RWGs | 5
40708 |  |  |  |  | 40708 | Timber generally (soffits/fascias) | 5
40709 |  |  |  |  | 40709 | Other | 5
40801 |  |  | 408 | Soffits / fascias | 40801 | Timber | 15 |  | m2
40802 |  |  |  |  | 40802 | PVCu | 25 |  | m2
40803 |  |  |  |  | 40803 | Aluminium | 30
40901 |  |  | 409 | Upper Floors | 40901 | Cast In-situ Concrete | 80 |  | m2
40902 |  |  |  |  | 40902 | Block & Beam | 80 |  | m2
40903 |  |  |  |  | 40903 | Steel | 85 |  | m2
40904 |  |  |  |  | 40904 | Suspended timber | 70
41001 |  |  | 410 | Windows (inc grilles/louvres) | 41001 | Powder Coated Aluminium | 45 |  | Nr
41002 |  |  |  |  | 41002 | Metal | 45 |  | Nr
41003 |  |  |  |  | 41003 | Softwood Timber | 35 |  | Nr
41004 |  |  |  |  | 41004 | PVCu Double Glazed Unit | 35 |  | Nr
41005 |  |  |  |  | 41005 | Alum. Louvres | 45
41006 |  |  |  |  | 41006 | Alum. Grilles | 45
41101 |  |  | 411 | Doors | 41101 | Powder Coated Aluminium | 30 |  | Nr
41102 |  |  |  |  | 41102 | PVCu Double Glazed Unit | 30 |  | Nr
41103 |  |  |  |  | 41103 | Glazed Doors | 30 |  | Nr
41104 |  |  |  |  | 41104 | Metal Lourve Door | 30 |  | Nr
41105 |  |  |  |  | 41105 | High Speed Fabric Door | 25 |  | Nr
41201 |  |  | 412 | Frame | 41201 | Concrete | 80 |  | m2
41202 |  |  |  |  | 41202 | Steel | 85 |  | m2
41203 |  |  |  |  | 41203 | L/B brickwork | 85
41301 |  |  | 413 | Roof frame | 41301 | Timber | 70
41302 |  |  |  |  | 41302 | Steel | 85
41401 |  |  | 414 | Stairs | 41401 | Concrete | 85 |  | Nr
41402 |  |  |  |  | 41402 | Steel | 85 |  | Nr
41501 |  |  | 415 | External canopies / structures | 41501 | Canopies fixed to block
41502 |  |  |  |  | 41502 | Freestading canopy
41503 |  |  |  |  | 41503 | Bike Shelter
41504 |  |  |  |  | 41504 | Smoking Shelter
41601 |  |  | 416 | Balustrades & Handrails | 41601 | Timber | 25 |  | lm
41602 |  |  |  |  | 41602 | Metal | 35 |  | lm
50101 | 5 | Fencing | 501 | Fencing & Security | 50101 | Concrete post & wire | 25 |  | m2
50102 |  |  |  |  | 50102 | Timber post & wire | 20 |  | m2
50103 |  |  |  |  | 50103 | Timber boards | 15 |  | m2
50104 |  |  |  |  | 50104 | Concrete posts | 25 |  | lm
50105 |  |  |  |  | 50105 | Chain link | 20 |  | lm
50106 |  |  |  |  | 50106 | Mild steel railings | 12 |  | lm
50107 |  |  |  |  | 50107 | Wrought iron railings | 25 |  | lm
50108 |  |  |  |  | 50108 | Galvanised/painted | 20 |  | lm
50109 |  |  |  |  | 50109 | Galanised security gates | 20 |  | Nr
50110 |  |  |  |  | 50110 | Other | x
60101 | 6 | Sub Structure | 601 | Foundations | 60101 | Concrete | 110 |  | lm
7

## Element look up - M+E
Element Ref: | ELEMENT | EG Ref: | ELEMENT GROUP | SE Ref: | SUB ELEMENT GROUP | INDICATIVE LIFE / YEARS | REDUCED LIFE DUE TO USAGE | STANDARD RATE | RATE TYPE/ Item, M2, Nr
1 | Mechanical Services | 101 | Heating Plant & Auxiliaries | 10101 | Gas fired boiler <100kw | 20 | 12 |  | Nr
|  |  |  | 10102 | Gas fired boiler 100kw - 300kw | 25 | 15 |  | Nr
|  |  |  | 10103 | Gas fired boiler 300kw - 500kw | 25 | 20 |  | Nr
|  |  |  | 10104 | Gas fired boiler 500kw + | 25 | 20 |  | Nr
|  |  |  | 10105 | Flue Systems (stainless steel 200 kw boiler) | 30 | 25 |  | Nr
|  |  |  | 10106 | Fan Flues Systems. | 25 | 15 |  | Item
|  |  |  | 10107 | Commerical Circulating Pump (Single or dual type) | 20 | 15 |  | Nr
|  |  |  | 10108 | Centrifugal pumps | 20 | 15 |  | Nr
|  |  |  | 10109 | Heating pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10110 | Combined heating / chilled water pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10111 | Expansion vessel (unvented hot water) | 15 | 10 |  | Nr
|  |  |  | 10112 | Gas fired warm air heaters. | 20 | 20 |  | Nr
|  |  |  | 10113 | Dosing pots | 15 | 15 |  | Nr
|  |  |  | 10114 | Sump and well pumps | 12 | 12 |  | Nr
|  |  |  | 10115 | Air-to-air commercial Heat pumps | 15 | 15 |  | Nr
|  |  |  | 10116 | Water-to-air commerical Heat pumps | 15 | 15 |  | Nr
|  |  |  | 10117 | Water treatment equipment | 15 | 15 |  | Item
|  | 102 | Heating Distribution | 10201 | Heating Distribution Pipework | 25 | 25 |  | m2
|  |  |  | 10202 | Heating Services thermal insulation | 30 | 30 |  | m2
|  |  |  | 10203 | Plant Manual Isolation Valves | 25 | 15 |  | Item
|  |  |  | 10204 | Radiators. | 20 | 20 |  | Nr
|  |  |  | 10205 | Radiant Panels | 20 | 20 |  | Nr
|  |  |  | 10206 | Fan Convectors | 20 | 15 |  | Nr
|  |  |  | 10207 | Natural Convectors | 20 | 20 |  | Nr
|  |  |  | 10208 | Underfloor heating steel pipes & Manifolds | 30 | 15 |  | m2
|  |  |  | 10209 | LTHW Warm air heaters | 15 | 15 |  | Nr
|  |  |  | 10210 | Electric Heaters. | 10 | 10 |  | Nr
|  |  |  | 10211 | Expansion Bellow. | 10 | 10 |  | Nr
[5 empty] | Motorised Actuators | 10
|  |  |  | 10212 | Steam Pipework system | 25 | 20 |  | m2
|  | 103 | Heating Controls | 10301 | Building Management Systems | 15 | 15 |  | Item
|  |  |  | 10302 | Control Panels | 20 | 15 |  | Nr
|  |  |  | 10303 | Motorised Control Valves | 15 | 15 |  | Nr
|  | 104 | Fuel Services | 10401 | Gas distribution pipework | 25 | 25 |  | m2
|  |  |  | 10402 | Oil distribution pipework | 25 | 25 |  | m2
|  |  |  | 10403 | Fuel Booster Pumps | 15 | 15 |  | Nr
|  |  |  | 10404 | Fuel shut-off valves | 25 | 20 |  | Nr
|  |  |  | 10405 | Fuel storage tank. | 20 | 20 |  | Nr
|  |  |  | 10406 | Medical Gases | 20 | 20 |  | m2
|  |  |  | 10407 | Fuel Meter & Measurement | 20 | 20 |  | Item
|  | 105 | Cold Water Plant & Equipment | 10501 | Mains cold water booster | 15 | 15 |  | Nr
|  |  |  | 10502 | Cold Water Storage Tanks | 25 | 20 |  | Nr
|  |  |  | 10503 | Sprinkler | 20 | 20 |  | m2
|  | 106 | Hot & Cold Water Distribution Services | 10601 | Hot and Cold Water Pipework systems | 25 | 25 |  | m2
|  |  |  | 10602 | Hot & Cold Water Services thermal insulation | 30 | 20 |  | m2
|  |  |  | 10603 | Hot water temperature mixing valve | 10 |  |  | Nr
|  |  |  | 10604 | Shower mixer and head | 10 | 10 |  | Nr
|  |  |  | 10605 | Water Meter & Measurement | 20 | 15 |  | Item
|  | 107 | Hot Water Plant & Equipment | 10701 | Calorifiers (Copper/ Mild Steel) | 20 | 15 |  | Nr
|  |  |  | 10702 | Circulating Pumps | 15 | 15 |  | Nr
|  |  |  | 10703 | Electric hot water heaters | 15 | 10 |  | Nr
|  |  |  | 10704 | Gas fired hot water heaters | 20 | 15 |  | Nr
|  |  |  | 10705 | Heat Exchanger (Plate / Shell and tube) | 20 | 10 |  | Nr
|  |  |  | 10706 | Water Boilers - (tea points) | 15 | 10 |  | Nr
|  | 108 | Mechanical Ventilation | 10801 | Packaged Air handling units | 20 | 20 |  | Nr
|  |  |  | 10802 | Roof mounted units fans | 15 | 15 |  | Nr
|  |  |  | 10803 | Axial fans (inline) | 15 | 15 |  | Nr
|  |  |  | 10804 | Centrifugal fans | 20 | 15 |  | Nr
|  |  |  | 10805 | Local extract fans | 10 | 10 |  | Nr
|  |  |  | 10806 | Stair / lobby ventilation | 20 | 20 |  | Item
|  |  |  | 10807 | Galvanised Ductwork Systems | 40 | 40 |  | m2
|  |  |  | 10808 | Ductwork thermal insulation | 30 | 30 |  | m2
|  |  |  | 10809 | External louvres steel painted | 20 | 20 |  | Nr
|  |  |  | 10810 | Fire Dampers | 10 | 10 |  | Nr
|  |  |  | 10811 | Grilles and diffusers | 25 | 25 |  | Nr
|  |  |  | 10812 | Humidifier | 15 | 15 |  | Nr
|  |  |  | 10813 | VAV terminal units | 15 | 15 |  | Nr
|  |  |  | 10814 | Kitchen Extract canopies/ Hoods (average) | 30 | 20 |  | Item
|  |  |  | 10815 | Ductwork Heating/ cooiling coils | 25 | 20 |  | Item
|  | 109 | Chilled Water Plant & Equipment | 10901 | Absorption / Centrifugal Chiller 100kw - 300kw | 25 | 20 |  | Nr
|  |  |  | 10902 | Absorption / Centrifugal Chiller 300kw - 500kw | 25 | 20 |  | Nr
|  |  |  | 10903 | Absorption / Centrifugal Chiller 500kw + | 25 | 20 |  | Nr
|  |  |  | 10904 | Circulating Commerical Pump (single or dual type) | 20 | 15 |  | Nr
|  |  |  | 10905 | Refrigerant leak detector | 10 | 10 |  | Item
|  |  |  | 10906 | Trace heating | 20 | 15 |  | m2
|  |  |  | 10907 | Air cooled/ Evaporative condensers | 20 | 15 |  | Nr
|  |  |  | 10908 | Chilled Water storage vessel | 20 | 20 |  | Nr
|  |  |  | 10909 | Chilled Water pressurisation unit | 20 | 20 |  | Nr
|  |  |  | 10910 | Chilled Water Pipework & Valve | 25 | 25 |  | m2
|  |  |  | 10911 | Chilled Water Services thermal insulation | 30 | 20 |  | m2
|  | 110 | Comfort Cooling | 11001 | Fan coil units (heating and cooling) | 15 | 15 |  | Nr
|  |  |  | 11002 | Split systems | 10 | 10 |  | Nr
|  |  |  | 11003 | Computer room air conditioning | 15 | 15 |  | Item
|  |  |  | 11004 | Air conditioning terminal units chilled beams | 20 | 20 |  | Nr
|  |  |  | 11005 | Refrigerant pipework systems | 30 | 30 |  | m2
|  |  |  | 11006 | Condensate pipework system | 15 | 15 |  | m2
|  |  |  | 11007 | VRV units | 15 | 15 |  | Nr
|  | 111 | Miscellaneous Mechanical Equipment & Plant | 11101 | Air compressor | 20 | 20 |  | Nr
|  |  |  | 11102 | Compressed air reciever | 20 | 20 |  | Nr
|  |  |  | 11103 | Pneumatic controls lampsom | 20 | 15 |  | Item
|  |  |  | 11104 | Other |  |  |  | Nr
2 | Electrical Services | 201 | Mains Power Supplies | 20101 | HV switchgear (external) | 30 | 30 |  | Item
|  |  |  | 20102 | Transformers (dry type) | 30 | 30 |  | Nr
|  |  |  | 20103 | LV switchgear (internal) | 25 | 25 |  | Item
|  |  |  | 20104 | Main supply switchgear | 30 | 30 |  | Item
|  |  |  | 20105 | SWA mains/sub distribution cables. | 35 | 35 |  | m2
|  |  |  | 20106 | Earth bonding (Primary) | 30 | 30 |  | Item
|  |  |  | 20107 | Electricity Meter & Measurement | 20 | 20 |  | Item
|  | 202 | Sub-Main Distribution | 20201 | Consumer units | 20 | 20 |  | Nr
|  |  |  | 20202 | Distribution boards (critical) | 20 | 20 |  | Nr
|  |  |  | 20203 | Distribution boards (Non critical) | 20 | 20 |  | Nr
|  |  |  | 20204 | Feeder pillar | 20 | 20 |  | Nr
|  |  |  | 20205 | Inverters | 10 | 10 |  | Nr
|  |  |  | 20206 | Sub distribution wiring and containment systems | 25 | 25 |  | m2
|  |  |  | 20207 | Fixed appliance power supplies/ isolators (Spurs) | 25 | 25 |  | Nr
|  |  |  | 20208 | Switched socket outlet (SSO) | 20 | 20 |  | Nr
|  | 203 | Lighting Systems | 20301 | Emergency lighting (inc key switch) | 25 | 20 |  | Nr
|  |  |  | 20302 | Lighting and luminaires (external) | 15 | 15 |  | Nr
|  |  |  | 20303 | Lighting and luminaires (internal) | 20 | 20 |  | Nr
|  |  |  | 20304 | Lighting control and management systems | 15 | 15 |  | Item
|  | 204 | Protection Systems | 20401 | Access control | 15 | 15 |  | Item
|  |  |  | 20402 | Closed Circuit Television (CCTV) | 20 | 15 |  | m2
|  |  |  | 20403 | Nurse Call Alarm | 15 | 15 |  | m2
|  |  |  | 20404 | Distress Call Alarm | 15 | 15 |  | Item
|  |  |  | 20405 | Fire Alarm Installations (inc, call points, sounders and detection) | 20 | 20 |  | m2
|  |  |  | 20406 | Computer room fire extinguishing system | 15 | 15 |  | m2
|  |  |  | 20407 | Wet/ Dry Riser | 25 | 25 |  | Item
|  |  |  | 20408 | Smoke ventilation systems | 30 | 30 |  | Item
|  |  |  | 20409 | Intruder alarms and intercommunications | 15 | 15 |  | m2
|  |  |  | 20410 | Lightning protection | 25 | 25 |  | m2
|  |  |  | 20411 | Leak Detection | 10 | 10 |  | m2
|  | 205 | Communication System | 20501 | Communication systems | 20 | 20 |  | m2
|  |  |  | 20502 | Public address systems | 20 | 15 |  | m2
|  |  |  | 20503 | Television and satelite systems | 15 | 15 |  | m2
|  | 206 | Lifting Equipment | 20601 | Lift Plant & Controls | 30 | 25 |  | Item
|  |  |  | 20602 | Lift Car refurbishment | 15 | 15 |  | Item
|  |  |  | 20603 | Stair Lifts | 20 | 15 |  | Item
|  |  |  | 20604 | Lifting Hoists | 20 | 15 |  | Item
|  | 207 | Power Generation | 20701 | Combined heat and power (CHP) (gas fired) | 20 | 15 |  | Nr
|  |  |  | 20702 | Standby genernator plus prime mover | 30 | 30 |  | Item
|  |  |  | 20703 | Uninterruptible power supply (UPS) systems | 20 | 20 |  | Item
|  | 208 | Miscellaneous Electrical Equipment & Plant | 20801 | Hand dryer | 5 | 5 |  | Nr
|  |  |  | 20802 | Incinerators | 15 | 15 |  | Item
|  |  |  | 20803 | Kitchen (cooking and support systems) | 15 | 15 |  | Item
|  |  |  | 20804 | Laundries (equipment and support systems) | 20 | 20 |  | Item
|  |  |  | 20805 | Photocoltaic panels | 25 | 25 |  | Nr
|  |  |  | 20806 | Open door with obstacle detector | 20 | 20 |  | Item
|  |  |  | 20807 | Mechanical Roller Shutter Doors | 15 | 15 |  | Item
|  |  |  | 20808 | Theatre clocks | 15 | 15 |  | Item
|  |  |  | 20809 | Other |  |  |  | Nr

## Master Sheet Summary
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Rowthorne HOP - 25 Yr Master Cost Plan
1 | Preliminaries | 1 | Item | 0 | 0
2 | Ceilings | 1 | Item | 0 | 0
3 | External walls, windows & Doors | 1 | Item | 142402 | 142402
4 | Floors and Stairs | 1 | Item | 146358 | 146358
5 | Internal Walls & Doors | 1 | Item | 85582 | 85582
6 | Redecorations | 1 | Item | 133729 | 133729
7 | Roofs | 1 | Item | 291737 | 291737
8 | Sanitary Services | 1 | Item | 98208 | 98208
9 | Fixed Furniture and Fittings | 1 | Item | 10040 | 10040
9 | External Areas | 1 | Item | 102165 | 102165
10 | Mechanical Services | 1 | Item | 152100 | 152100
11 | Electrical Services | 1 | Item | 94000 | 94000
12 | Sub-total |  |  |  | 1256321
.
13 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 188448.15
.
14 | Preliminaries Site Specific Costs (scaffold etc,,,) |  |  |  | 30000
15 | Provisional Uplift for Sectional Works @ 25% |  |  |  | 368692.2875
16 | Sub-total |  |  |  | 1843461.4375
17 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 0
18 | Sub-total |  |  |  | 1843461.4375
19 | Contractor Management Fee @ 3.25% |  |  |  | 0
20 | Sub-total |  |  |  | 1843461.4375
21 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 276519.2156
22 | Sub-total |  |  |  | 2119980.6531
23 | Risk Allowance @ 10% |  |  |  | 211998.0653
24 | Client Contingency @10% |  |  |  | 211998.0653
25 | Sub-total |  |  |  | 2543976.7838
26 | Professional fees, surveys and stat fees (15%) |  |  |  | 381596.5176
27 | Total Construction Cost |  |  |  | 2925573.3013
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.
Note: Provisional uplift of 25% for sectional works included. Actual uplift would need to be established on a site by site basis based on the site layout, extent of works required and the practicalities of undertaking that works with minimal disrupion.

## Roofing
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Ladycross House
Roofing Project Works
1 | Preliminaries | 1 | Item |  | 0
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 0 | 0
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1300 | m2 | 5 | 6500
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 1500 | 1500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 2500 | 2500
3 | Roofs | 1 | Item | 291737 | 291737
3.01 | Recovering the existing felt flat roof, including all insulation, flashings and rainwater goods. |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
11 | Sub-total |  |  |  | 291737
.
12 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 43760.55
.
13 | Preliminaries Site Specific Costs |  |  |  | 0
14 | Sub-total |  |  |  | 335497.55
15 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 10903.6704
16 | Sub-total |  |  |  | 346401.2204
17 | Contractor Management Fee @ 3.25% |  |  |  | 11258.0397
18 | Sub-total |  |  |  | 357659.26
19 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 53648.889
20 | Sub-total |  |  |  | 411308.149
21 | Risk Allowance @ 10% |  |  |  | 41130.8149
22 | Client Contingency @10% |  |  |  | 41130.8149
23 | Sub-total |  |  |  | 493569.7789
24 | Scape Fee @ 0.95% |  |  |  | 4688.9129
25 | Total Construction Cost |  |  |  | 498258.6918
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.

## Room refurbishment
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Ladycross House
Room Refurbishment Project Works
1 | Preliminaries | 1 | Item |  | 0
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 5302.5 | 5302.5
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1400 | m2 | 5 | 7000
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 500 | 500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 1000 | 1000
2 | Internal Walls, Ceilings and Doors | 1 | Item | 85582 | 85582
2.01 | Include for all internal finishes that are life expired, unon-compliant or do not meet the suitability requirements |  | Note
2.02 | See full condition survey data and summary report for further cost break down. |  | Note
3 | Floors and Stairs | 1 | Item | 146358 | 146358
3.01 | Sumarise required works |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
4 | Fixed furniture and fittings | 1 | Item | 10040 | 10040
4.01 | Sumarise required works |  | Note
4.02 | See full condition survey data and summary report for further cost break down. |  | Note
5 | Decorations | 1 | Item | 133729 | 133729
5.01 | Sumarise required works |  | Note
5.02 | See full condition survey data and summary report for further cost break down. |  | Note
6 | Sub-total |  |  |  | 241980
.
7 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 36297
.
8 | Preliminaries Site Specific Costs |  |  |  | 0
9 | Sub-total |  |  |  | 278277
10 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 9044.0025
11 | Sub-total |  |  |  | 287321.0025
12 | Contractor Management Fee @ 3.25% |  |  |  | 9337.9326
13 | Sub-total |  |  |  | 296658.9351
14 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 44498.8403
15 | Sub-total |  |  |  | 341157.7753
16 | Risk Allowance @ 10% |  |  |  | 34115.7775
17 | Client Contingency @10% |  |  |  | 34115.7775
18 | Sub-total |  |  |  | 409389.3304
19 | Scape Fee @ 0.95% |  |  |  | 3889.1986
20 | Total Construction Cost |  |  |  | 413278.5291
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.

## M&E critical works
DERBYSHIRE COUNTY COUNCIL
Estimate Cost Plan -Ladycross House
2018-01-01
Item | Description of Work | Quantity | Unit | Cost | Total Cost
Ladycross House
Mechanical and Electrial works package
1 | Preliminaries | 1 | Item |  | 16802.5
1.01 | The contractor is to provide safe and sufficient scaffolding access with safety guardrails to enable full access to all areas of work. | 1 | Item | 5302.5 | 5302.5
1.02 | The contractor is to provide suitable and sufficient protection of property and people for the duration of the works. | 1400 | m2 | 5 | 7000
1.03 | The contractor is to allow for cleaning ensuring all debris is removed from site, including making good of damaged surfaces. | 1 | Psum | 500 | 500
1.04 | The contractor to allow for the provision of skips for the removal of all waste materials. | 10 | Item | 300 | 3000
1.05 | The contractor to allow for the removal and reinstatement of all external fixtures and fittings. | 1 | Psum | 1000 | 1000
2 | Mechanical Services | 1 | Item | 152100 | 152100
2.01 | Replacement of fan coiled units to A Block, undertake detailed review of heating controls to A Block and cleaning of mechanical extract in toilet areas in A Block and B Block. |  | Note
2.02 | See full condition survey data and summary report for further cost break down. |  | Note
3 | Electrical Services | 1 | Item | 94000 | 94000
3.01 | Replace existing light fitting with new LED and replace life expired fire alarm systems to A and B Block. |  | Note
3.02 | See full condition survey data and summary report for further cost break down. |  | Note
4 | Builders work in connection | 1 | Item | 0 | 0
4.01 | Take down ceilings, reinsate compartmentation etc… |  | Note
4.02 | See full condition survey data and summary report for further cost break down. |  | Note
5 | Sub-total |  |  |  | 246100
.
6 | Preliminaries People and Equipment (Based on 15%) |  |  |  | 36915
.
7 | Preliminaries Site Specific Costs |  |  |  | 16802.5
8 | Sub-total |  |  |  | 299817.5
9 | Pre Construction costs:EMPA @ 3.25% |  |  |  | 9744.0688
10 | Sub-total |  |  |  | 309561.5687
11 | Contractor Management Fee @ 3.25% |  |  |  | 10060.751
12 | Sub-total |  |  |  | 319622.3197
13 | Statutory and consultancy fees (includes Building Control, Building Surveyor, Building Services, surveys etc.) @ 15% |  |  |  | 47943.348
14 | Sub-total |  |  |  | 367565.6677
15 | Risk Allowance @ 10% |  |  |  | 36756.5668
16 | Client Contingency @10% |  |  |  | 36756.5668
17 | Sub-total |  |  |  | 441078.8012
18 | Scape Fee @ 0.95% |  |  |  | 4190.2486
19 | Total Construction Cost |  |  |  | 445269.0498
Note: All costs to be read in conjunctions with the list of assumptions and clarifications as defined within the report, as well as the information detailed within the report wording.